## Legend
Introduction
DOCUMENT INFORMATION
This document contains all the informations of ATS022 available with an external commmunication net.
All the informations are managed in 3 different sheets: - Map: list of all the registers and address for Modbus RTU communication protocol. - Tables: list of tables not reported on "map" sheet.
NOTE: all the changes are reported on "Revision History" sheet.
Application Note
MODBUS FUNCTIONS
ATS022 supports following Modbus functions:
NOTE: - Addr= Device address (see slave address=604) - Byte Count= Num of registers * 2 - All data must bne inserted in headecimal value
FUNCTIONS MANAGEMENT FOR ATS022
NOTE: all examples here follow with parameters: device address= 1; without CRC
ATS022 incudes some function limitation for Commands (register address= 0): - Commands from 1 to 31 work correctly both with function 6 and 16. Example: Start Generator command can be send both with function 6 (Query: 01.06.00.00.00.1E) and 16 (Query: 01.10.00.00.00.01.02.00.1E). - Open/Close/Abort programming session commands work correctly with function 16: Example: Open programming session command must be managed only with function 16 (Query: 01.10.00.00.00.01.02.00.64).
ATS022 incudes some indications for Write Multiple Registers function (function 16): - Function 16 can be used directely for commands (register address= 0). Example: Stop Generator command= Query: 01.10.00.00.00.01.02.00.1F. - Function 16 for all the others available registers must be managed in a programming session: Open programming Session command (Query 1) + function 16 of the wished parameters (Query 2) + Close programming Session command (Query 3). Example: New password setting (register address= 630; new value= 5): Query 1: 01.10.00.00.00.01.02.00.64 + Query 2: 01.10.02.76.00.01.02.00.05 + Query 3: 01.10.00.00.00.01.02.00.65.
EVENTS
In case of Event type (byte 15=1), bits from 0 to 7 refer to modality at the recording time: Not significant: not recorded Manual: Action was done in manual mode (CB closed by pushing a button for example) Auto: Action was done by automatic control sequence Test: Action was done in test sequence External command: Action was not done by using ATS022 (CB status changed manually for example) Fieldbus: Action was done via a Modbus command Digital input: Action was done by activating a digital input
Acronym and definition
Measure units | Meaning
s | Second
Hz | Hertz
V | Volt
General | Meaning
CB | circuit breaker
Copyright
The data and illustrations are not binding. We reserve the right to modify the contents of this document on the basis of technical development of the products, without prior notice.
Copyright 2000-2016 ABB. All rights reserved.

## Revision History
Release | Date | Description
A | 2011-10-12 | First Release
B | 2013-08-09 | Modbus registers for Delay TL (908) and DO7 Safety Load (639) added . Events SLC On and SLC Off added.(available for 2G SW version or higher)
C | 2014-09-10 | - New template - Inserted Modbus functions list in Legend sheet
D | 2016-05-24 | Inserted Copyright notes in Legend sheet
E | 2016-09-01 | events safet load: inserted details (acronyms)
F | 2017-05-04 | Events: updated main table; new details in legend; new sheet for automatic conversion

## Map
Registers & Parameters Name | Number of registers | Bitfield | Range | Description | Units | Multiplier | Data Type | Read Write | Modbus
[9 empty] | Register Address (DEC) | Register Address (HEX) | 03 | 04 | 06 | 16
Commands | 1 | [7 empty] | 0 | 0000
Command type | 1 |  | Commands |  |  | 1 | UINT | W | 0 | 0000 |  |  | x | x
Status | 1 | [7 empty] | 40 | 0028
Global | 1 | x |  |  |  | 1 | UINT | R | 40 | 0028 | x | x
LN1 status |  | 0 | LN1 status | The conbination of the 3bits allow to manage the 8 status (see the proper table)
LN1 status |  | 1
LN1 status |  | 2
LN2 status |  | 3 | LN2 status | The conbination of the 3bits allow to manage the 8 status (see the proper table)
LN2 status |  | 4
LN2 status |  | 5
Switching status |  | 6 | SWITCHING STATUS | The conbination of the 3bits allow to manage the 5 status (see the proper table)
Switching status |  | 7
Switching status |  | 8
Generator status |  | 9 | 0: stopped, 1: started
10
11
12
13
14
15
Alarms | 1 | x | 158 |  |  | 1 | UINT | R | 54 | 0036 | x | x
CB1 OPEN FAILURE |  | 0 | 0: no alarm, 1: alarm
CB2 OPEN FAILURE |  | 1 | 0: no alarm, 1: alarm
CB3 OPEN FAILURE |  | 2 | 0: no alarm, 1: alarm
CB1 CLOSE FAILURE |  | 3 | 0: no alarm, 1: alarm
CB2 CLOSE FAILURE |  | 4 | 0: no alarm, 1: alarm
CB3 CLOSE FAILURE |  | 5 | 0: no alarm, 1: alarm
CB1 EXTRACTED |  | 6 | 0: no alarm, 1: alarm
CB2 EXTRACTED |  | 7 | 0: no alarm, 1: alarm
LOGIC LOCKED |  | 8 | 0: no alarm, 1: alarm
EXTERNAL FAULT |  | 9 | 0: no alarm, 1: alarm
CB1 TRIPPED |  | 10 | 0: no alarm, 1: alarm
CB2 TRIPPED |  | 11 | 0: no alarm, 1: alarm
GENERATOR ALARM |  | 12 | 0: no alarm, 1: alarm
13
14
15
Digital inputs | 10 |  |  |  |  | 1 | UINT |  | 58 | 003A
CB1 Status | 1 | x | CB1 status |  |  | 1 | UINT | R | 58 | 003A | x | x
CB2 Status | 1 | x | CB2 status |  |  | 1 | UINT | R | 59 | 003B | x | x
CB3 Status | 1 |  | 0: open, 1: closed |  |  | 1 | UINT | R | 60 | 003C | x | x
Generator Alarm | 1 |  | 0: no alarm, 1: alarm |  |  | 1 | UINT | R | 61 | 003D | x | x
Logic Locked | 1 |  | 0: enabled, 1: locked |  |  | 1 | UINT | R | 62 | 003E | x | x
Force Commutation | 1 |  | 0: inactive, 1: active |  |  | 1 | UINT | R | 63 | 003F | x | x
Generator Start | 1 |  | 0: inactive, 1: active |  |  | 1 | UINT | R | 64 | 0040 | x | x
Switching Enabled | 1 |  | 0: enabled, 1: disabled |  |  | 1 | UINT | R | 65 | 0041 | x | x
Remote Reset | 1 |  | 0: inactive, 1: active |  |  | 1 | UINT | R | 66 | 0042 | x | x
Emergency Lock | 1 |  | 0: inactive, 1: active |  |  | 1 | UINT | R | 67 | 0043 | x | x
Voltages measures | 12 | [7 empty] | 150 | 0096
LN1 V1 Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 150 | 0096 | x | x
LN1 V2Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 152 | 0098 | x | x
LN1 V3 Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 154 | 009A | x | x
LN1 V12 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 158 | 009E | x | x
LN1 V23 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 160 | 00A0 | x | x
LN1 V31 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 162 | 00A2 | x | x
LN2 V1 Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 164 | 00A4 | x | x
LN2 V2Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 166 | 00A6 | x | x
LN2 V3 Voltage | 1 |  | 0…800V step 0.1V | Line to Neutral Voltage | V | 10 | UINT | R | 168 | 00A8 | x | x
LN2 V12 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 172 | 00AC | x | x
LN2 V23 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 174 | 00AE | x | x
LN2 V31 Voltage | 1 |  | 0…1400V step 0.1V | Line to Line Voltage | V | 10 | UINT | R | 176 | 00B0 | x | x
Other measures | 2 | [7 empty] | 250 | 00FA
LN1 Frequency | 1 |  | 0…450 Hz step 0.1 Hz | Maximum Frequency on LN1 | Hz | 10 | UINT | R | 250 | 00FA | x | x
LN2 Frequency | 1 |  | 0…450 Hz step 0.1 Hz | Maximum Frequency on LN2 | Hz | 10 | UINT | R | 252 | 00FC | x | x
Information A | 2 | [7 empty] | 500 | 01F4
Slave ID | 1 |  | 49 |  |  | 1 | UINT | R | 500 | 01F4 | x | x
SW version | 1 |  | byte 1: number, byte 0: letter (ASCII codes) |  |  | 1 | UINT | R | 501 | 01F5 | x | x
Information B | 8 | [7 empty] | 560 | 0230
Serial number digit 0 | 1 |  |  |  |  | 1 | UINT | R | 560 | 0230 | x | x
Serial number digit 1 | 1 |  |  |  |  | 1 | UINT | R | 561 | 0231 | x | x
Serial number digit 2 | 1 |  |  |  |  | 1 | UINT | R | 562 | 0232 | x | x
Serial number digit 3 | 1 |  |  |  |  | 1 | UINT | R | 563 | 0233 | x | x
Serial number digit 4 | 1 |  |  |  |  | 1 | UINT | R | 564 | 0234 | x | x
Serial number digit 5 | 1 |  |  |  |  | 1 | UINT | R | 565 | 0235 | x | x
Serial number digit 6 | 1 |  |  |  |  | 1 | UINT | R | 566 | 0236 | x | x
Serial number digit 7 | 1 |  |  |  |  | 1 | UINT | R | 567 | 0237 | x | x
Configuration parameters B | 26 | [7 empty] | 600 | 0258
Operating mode | 1 |  | Operating Mode |  |  | 1 | UINT | R/W | 600 | 0258 | x | x | x | x
Slave address | 1 |  | 1 … 247 step 1 |  |  | 1 | UINT | R/W | 604 | 025C | x | x | x | x
Baud rate | 1 |  | Baud rate |  |  | 1 | UINT | R/W | 605 | 025D | x | x | x | x
Protocol type | 1 |  | Protocol type |  |  | 1 | UINT | R/W | 606 | 025E | x | x | x | x
Tag name letter 0 | 1 |  | ASCII code |  |  | 1 | UINT | R/W | 607 | 025F | x | x | x | x
Tag name letter 1 | 1 |  | ASCII code |  |  | 1 | UINT | R/W | 608 | 0260 | x | x | x | x
Tag name letter 2 | 1 |  | ASCII code |  |  | 1 | UINT | R/W | 609 | 0261 | x | x | x | x
Tag name letter 3 | 1 |  | ASCII code |  |  | 1 | UINT | R/W | 610 | 0262 | x | x | x | x
Tag name letter 4 | 1 |  | ASCII code |  |  | 1 | UINT | R/W | 611 | 0263 | x | x | x | x
Device Status | 1 |  | Device status |  |  | 1 | UINT | R/W | 622 | 026E | x | x | x | x
Line 1 Configuration | 1 |  | 0: 1 phase, 1: 3 phases without N, 2: 3 phases with N |  |  | 1 | UINT | R/W | 623 | 026F | x | x | x | x
Nominal Voltage | 1 |  | Nominal Voltage |  |  | 1 | UINT | R/W | 624 | 0270 | x | x | x | x
Frequency | 1 |  | 0= 16Hz; 1=50Hz; 2=60Hz; 3=400Hz |  |  | 1 | UINT | R/W | 625 | 0271 | x | x | x | x
Protection Devices | 1 |  | Protection Device |  |  | 1 | UINT | R/W | 626 | 0272 | x | x | x | x
Genrator usage | 1 |  | 0: not in use, 1: in use |  |  | 1 | UINT | R/W | 627 | 0273 | x | x | x | x
Line Priority | 1 |  | 0: no priority, 1: line 1 priority, 2: line 2 priority |  |  | 1 | UINT | R/W | 628 | 0274 | x | x | x | x
Language | 1 |  | 0: English, 1: German, 2: French, 3: Italian, 4: Spanish, 5: Finnish, 6: Russian, 7: Chinese |  |  | 1 | UINT | R/W | 629 | 0275 | x | x | x | x
User Password | 1 |  | 0000….9999 step 1 |  |  | 1 | UINT | R/W | 630 | 0276 | x | x | x | x
Ext VT Trafo | 1 |  | 0=absent; 1=present |  |  | 1 | UINT | R/W | 631 | 0277 | x | x | x | x
Ext VT Primary | 1 |  | Primary Voltage |  |  | 1 | UINT | R/W | 632 | 0278 | x | x | x | x
Ext VT Secondary | 1 |  | Secondary Voltage |  |  | 1 | UINT | R/W | 633 | 0279 | x | x | x | x
Line 2 Configuration | 1 |  | 0: 1 phase, 1: 3 phases without N, 2: 3 phases with N |  |  | 1 | UINT | R/W | 634 | 027A | x | x | x | x
Switching Configuration | 1 |  | 0: with back switching, 1: without back switching |  |  | 1 | UINT | R/W | 635 | 027B | x | x | x | x
DI10 Configuration | 1 |  | 0: generator start, 1: switch enable, 2: remote reset, 3: emergency lock, 4: disabled |  |  | 1 | UINT | R/W | 636 | 027C | x | x | x | x
DI10 Contact type | 1 |  | 0= NO; 1= NC |  |  | 1 | UINT | R/W | 637 | 027D | x | x | x | x
DI8 contact type | 1 |  | 0= NO; 1= NC |  |  | 1 | UINT | R/W | 638 | 027E | x | x | x | x
DO7 Safety Load | 1 |  | Safety load bits |  |  | 1 | UINT | R/W | 639 | 027F | x | x | x | x
Set V_threshold | 1 | [7 empty] | 881 | 0371
Threshold Vmin | 1 |  | -30%...-5% step 1% |  | % | 1 | UINT | R/W | 881 | 0371 | x | x | x | x
Threshold Vmax | 1 |  | 5%...30% step 1% |  | % | 1 | UINT | R/W | 882 | 0372 | x | x | x | x
Set F_threshold | 1 | [7 empty] | 891 | 037B
Threshold Fmin | 1 |  | -10%...-1% step 1% |  | % | 1 | UINT | R/W | 891 | 037B | x | x | x | x
Threshold Fmax | 1 |  | 1%...10% step 1% |  | % | 1 | UINT | R/W | 892 | 037C | x | x | x | x
Set Time | 6 | [7 empty] | 901 | 0385
Delay Ts | 1 |  | 0...30s step 1s |  | s | 1 | UINT | R/W | 901 | 0385 | x | x | x | x
Delay TCE | 1 |  | 0...60s step 1s |  | s | 1 | UINT | R/W | 902 | 0386 | x | x | x | x
Delay TBS | 1 |  | 0...59s step 1s, 1...30min step 1min |  | s | 1 | UINT | R/W | 903 | 0387 | x | x | x | x
Delay TCN | 1 |  | 0...60s step 1s |  | s | 1 | UINT | R/W | 904 | 0388 | x | x | x | x
Delay TGOFF | 1 |  | 0...59s step 1s, 1...30min step 1min |  | s | 1 | UINT | R/W | 905 | 0389 | x | x | x | x
Delay TC | 1 |  | 0...60s step 1s |  | s | 1 | UINT | R/W | 906 | 038A | x | x | x | x
Delay LCD Timer | 1 |  | 0...59s step 1s, 1...60min step 1min |  | s | 1 | UINT | R/W | 907 | 038B | x | x | x | x
Delay TL | 1 |  | 0...60s step 1s |  | s | 1 | UINT | R/W | 908 | 038C | x | x | x | x
Alarm/Event Log | 50 | [7 empty] | 2000 | 07D0
Alarm/Event 1 (newest) | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2000 | 07D0 | x | x
Alarm/Event 2 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2001 | 07D1 | x | x
Alarm/Event 3 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2002 | 07D2 | x | x
Alarm/Event 4 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2003 | 07D3 | x | x
Alarm/Event 5 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2004 | 07D4 | x | x
Alarm/Event 6 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2005 | 07D5 | x | x
Alarm/Event 7 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2006 | 07D6 | x | x
Alarm/Event 8 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2007 | 07D7 | x | x
Alarm/Event 9 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2008 | 07D8 | x | x
Alarm/Event 10 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2009 | 07D9 | x | x
Alarm/Event 11 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2010 | 07DA | x | x
Alarm/Event 12 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2011 | 07DB | x | x
Alarm/Event 13 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2012 | 07DC | x | x
Alarm/Event 14 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2013 | 07DD | x | x
Alarm/Event 15 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2014 | 07DE | x | x
Alarm/Event 16 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2015 | 07DF | x | x
Alarm/Event 17 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2016 | 07E0 | x | x
Alarm/Event 18 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2017 | 07E1 | x | x
Alarm/Event 19 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2018 | 07E2 | x | x
Alarm/Event 20 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2019 | 07E3 | x | x
Alarm/Event 21 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2020 | 07E4 | x | x
Alarm/Event 22 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2021 | 07E5 | x | x
Alarm/Event 23 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2022 | 07E6 | x | x
Alarm/Event 24 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2023 | 07E7 | x | x
Alarm/Event 25 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2024 | 07E8 | x | x
Alarm/Event 26 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2025 | 07E9 | x | x
Alarm/Event 27 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2026 | 07EA | x | x
Alarm/Event 28 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2027 | 07EB | x | x
Alarm/Event 29 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2028 | 07EC | x | x
Alarm/Event 30 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2029 | 07ED | x | x
Alarm/Event 31 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2030 | 07EE | x | x
Alarm/Event 32 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2031 | 07EF | x | x
Alarm/Event 33 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2032 | 07F0 | x | x
Alarm/Event 34 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2033 | 07F1 | x | x
Alarm/Event 35 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2034 | 07F2 | x | x
Alarm/Event 36 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2035 | 07F3 | x | x
Alarm/Event 37 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2036 | 07F4 | x | x
Alarm/Event 38 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2037 | 07F5 | x | x
Alarm/Event 39 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2038 | 07F6 | x | x
Alarm/Event 40 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2039 | 07F7 | x | x
Alarm/Event 41 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2040 | 07F8 | x | x
Alarm/Event 42 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2041 | 07F9 | x | x
Alarm/Event 43 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2042 | 07FA | x | x
Alarm/Event 44 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2043 | 07FB | x | x
Alarm/Event 45 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2044 | 07FC | x | x
Alarm/Event 46 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2045 | 07FD | x | x
Alarm/Event 47 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2046 | 07FE | x | x
Alarm/Event 48 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2047 | 07FF | x | x
Alarm/Event 49 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2048 | 0800 | x | x
Alarm/Event 50 | 1 | x | Alarm/event bits |  |  | 1 | UINT |  | 2049 | 0801 | x | x
Test Date | 3 | [7 empty] | 7009 | 1B61
Test Day | 1 |  | 1…31 |  |  | 1 | UINT | R/W | 7009 | 1B61 | x | x
Test Month | 1 |  | 1…12 |  |  | 1 | UINT | R/W | 7010 | 1B62 | x | x
Test Year | 1 |  | 2011…9999 |  |  | 1 | UINT | R/W | 7011 | 1B63 | x | x

## Tables
Baud rate |  | Protocol Type |  | Operating Mode |  | Public Commands |  |  | LN1 STATUS |  | LN2 STATUS |  | SWITCHING STATUS |  | Nominal Voltage |  | CB1 Status |  | CB1 Status |  | Device Status |  | Protection Device |  | Primary Voltage |  | Alarm/Event |  |  | Safety Load
0 | 9600 | 0 | E,8,1 | 0 | Local | Type | Value | Parameters | 0 | voltage ok | 0 | voltage ok | 0 | Sequence not required | 0 | 100/57 | bit 0 | 0: open, 1: closed | bit 0 | 0: open, 1: closed | 0 | auto | 0 | cbs | 0 | 100/57 | bit 15 = 0 | bit 0 | CB1 open failure | bit 0 | Undervoltage (1
1 | 19200 | 1 | O,8,1 | 1 | Remote |  |  |  | 1 | no voltage | 1 | no voltage | 1 | Sequence in progress | 1 | 115/66 | bit 1 | 0: inserted, 1: withdrawn | bit 1 | 0: inserted, 1: withdrawn | 1 | manual | 1 | bus tie | 1 | 115/66 | Alarm | bit 1 | CB2 open failure | bit 1 | Overvoltage (1
|  | 2 | N,8,2 |  |  | RESET (as RESET button) | 1 |  | 2 | undervoltage, | 2 | undervoltage, | 2 | Sequence completed | 2 | 120/70 | bit 2 | 0: not tripped, 1: tripped | bit 2 | 0: not tripped, 1: tripped | 2 | test | 2 | NPL bus tie | 2 | 120/70 |  | bit 2 | CB3 open failure | bit 2 | Phase missing (1
|  | 3 | N,8,1 | [5 empty] | 3 | overvoltage, | 3 | overvoltage, | 3 | Sequence rev in progress | 3 | 208/120 |  |  |  |  | 3 | powersave | 3 | NPL feeder open & close | 3 | 208/120 |  | bit 3 | CB1 close failure | bit 3 | Unbalance (1
[6 empty] | OPEN CB 1 | 7 |  | 4 | phase missing | 4 | phase missing | 4 | Sequence failed | 4 | 220/127 |  |  |  |  | 4 | generator test | 4 | NPL feeder only open | 4 | 220/127 |  | bit 4 | CB2 close failure | bit 4 | Incorrect phase seq (1
[6 empty] | CLOSE CB 1 | 8 |  | 5 | phase unbalance | 5 | phase unbalance |  |  | 5 | 230/132 | [8 empty] | 5 | 230/132 |  | bit 5 | CB3 close failure | bit 5 | Invalid frequency (1
[9 empty] | 6 | invalid phase order | 6 | invalid phase order |  |  | 6 | 240/138 | [8 empty] | 6 | 240/138 |  | bit 6 | CB1 extracted | 1) 0: inactive, 1: active
[6 empty] | TEST (as TEST button) | 13 |  | 7 | frequency out of range | 7 | frequency out of range |  |  | 7 | 277/160 | [8 empty] | 7 | 277/160 |  | bit 7 | CB2 extracted
[6 empty] | OPEN CB 2 | 14 | [7 empty] | 8 | 347/200 | [8 empty] | 8 | 347/200 |  | bit 8 | Logic locked
[6 empty] | CLOSE CB 2 | 15 | [7 empty] | 9 | 380/220 | [8 empty] | 9 | 380/220 |  | bit 9 | External fault
[15 empty] | 10 | 400/230 | [8 empty] | 10 | 400/230 |  | bit 10 | CB1 tripped
[6 empty] | OPEN CB 3 | 21 | [7 empty] | 11 | 415/240 | [8 empty] | 11 | 415/240 |  | bit 11 | CB2 tripped
[6 empty] | CLOSE CB 3 | 22 | [7 empty] | 12 | 440/254 | [8 empty] | 12 | 440/254 |  | bit 12 | Generator alarm
[15 empty] | 13 | 480/277 | [8 empty] | 13 | 480/277 |  | bit 13 | Not used
[6 empty] | Start Generator | 30 | [17 empty] | 14 | 500/288 |  | bit 14 | Not used
[6 empty] | Stop Generator | 31 | [17 empty] | 15 | 550/317 | bit 15 = 1 | bits 0…7 | 0 = not significant
[25 empty] | 16 | 600/347 | Event | Event mode | 1 = manual
[6 empty] | Open Programming Session | 100 | [17 empty] | 17 | 660/380 |  |  | 2 = auto
[6 empty] | Close Programming Session | 101 | [17 empty] | 18 | 690/400 |  |  | 3 = test
[6 empty] | Abort Programming Session | 102 | [17 empty] | 19 | 910/525 |  |  | 4 = external command
[25 empty] | 20 | 950/550 |  |  | 5 = fieldbus
[25 empty] | 21 | 1000/577 |  |  | 6 = digital input
[25 empty] | 22 | 1150/660 |  | bits 8…14 | 0 = LN1 no voltage
[28 empty] | Event code | 1 = LN1 undervoltage
2 = LN1 overvoltage
3 = LN1 phase missing
4 = LN1 voltage unbalance
5 = LN1 incorrect phase sequence
6 = LN1 invalid frequency
7 = LN2 no voltage
8 = LN2 undervoltage
9 = LN2 overvoltage
10 = LN2 phase missing
11 = LN2 voltage unbalance
12 = LN2 incorrect phase sequence
13 = LN2 invalid frequency
14 = Opening CB1
15 = Closing CB2
16 = Opening CB2
17 = Closing CB1
18 = CB1 open
19 = CB2 open
20 = CB3 open
21 = CB1 closed
22 = CB2 closed
23 = CB3 closed
24 = Generator started
25 = Generator stopped
26 = Logic enabled
27 = Logic disabled
28 = Force commutation on
29 = Force commutation off
30 = Generator start on
31 = Generator start off
32 = Switching enabled
33 = Switching disabled
34 = Remote reset on
35 = Remote reset off
36 = Manual to auto
37 = Auto to manual
38 = Manual to test
39 = Test to manual
40 = Opening CB3
41 = Closing CB3
42 = Emergency lock on
43 = Emergency lock off
44 = Safety Load On (SLC ON)
45 = Safety Load Off (SLC OFF)

## Events traslation
Read data (Hex):
caoncatenate event o alarm
num char | char completo | byte 1 | byte 2 | bin1 | bin2 | bit 15 | bit 15 text | intestazione 1 | intestazione 2
0 | 0 | 0 | 0 | 0 | 0 | 0 | Alarm | List of Alarms:
| 63 | 31 | 15 | 7 | 3 | 1 | 0 | 127 | 63 | 31 | 15 | 7 | 3 | 1 | 0
| bit 14 | bit 13 | bit 12 | bit 11 | bit 10 | bit 9 | bit 8 | bit 7 | bit 6 | bit 5 | bit 4 | bit 3 | bit 2 | bit 1 | bit 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
alarm | Not used | Not used | Generator alarm | CB2 tripped | CB1 tripped | External fault | Logic locked | CB2 extracted | CB1 extracted | CB3 close failure | CB2 close failure | CB1 close failure | CB3 open failure | CB2 open failure | CB1 open failure
allarmi in base a maschera
concatenate
event | bit 0…7 | 0 | Mode not significant / not recorded
| bit 8…14 | 0 | LN1 no voltage
0 | Mode not significant / not recorded | 0 | LN1 no voltage
1 | Manual | 1 | LN1 undervoltage
2 | Auto | 2 | LN1 overvoltage
3 | Test | 3 | LN1 phase missing
4 | External command | 4 | LN1 voltage unbalance
5 | Fieldbus | 5 | LN1 incorrect phase sequence
6 | Digital input | 6 | LN1 invalid frequency
|  | 7 | LN2 no voltage
|  | 8 | LN2 undervoltage
|  | 9 | LN2 overvoltage
|  | 10 | LN2 phase missing
|  | 11 | LN2 voltage unbalance
|  | 12 | LN2 incorrect phase sequence
|  | 13 | LN2 invalid frequency
|  | 14 | Opening CB1
|  | 15 | Closing CB2
|  | 16 | Opening CB2
|  | 17 | Closing CB1
|  | 18 | CB1 open
|  | 19 | CB2 open
|  | 20 | CB3 open
|  | 21 | CB1 closed
|  | 22 | CB2 closed
|  | 23 | CB3 closed
|  | 24 | Generator started
|  | 25 | Generator stopped
|  | 26 | Logic enabled
|  | 27 | Logic disabled
|  | 28 | Force commutation on
|  | 29 | Force commutation off
|  | 30 | Generator start on
|  | 31 | Generator start off
|  | 32 | Switching enabled
|  | 33 | Switching disabled
|  | 34 | Remote reset on
|  | 35 | Remote reset off
|  | 36 | Manual to auto
|  | 37 | Auto to manual
|  | 38 | Manual to test
|  | 39 | Test to manual
|  | 40 | Opening CB3
|  | 41 | Closing CB3
|  | 42 | Emergency lock on
|  | 43 | Emergency lock off
|  | 44 | Safety Load On (SLC ON)
|  | 45 | Safety Load Off (SLC OFF)