## Slide 1: GSec
SF6 load-break switch-disconnector
PPMV – Product Management

## Slide 2: GSec
Three position switch disconnector
Upper terminal
Lower terminal
Capacitive dividers intergrated
SF6 line disconnector
Insulate busbar from cables
SF6 earthing switch Grounds cable side
Notes: Audioscript: HySec connections are made through an upper terminal and a lower terminal. The lower terminal is composed by epoxy resin bushing with integrated capacitive dividers.
Audioscript_1: The vacuum interrupter is located in the upper part of the apparatus to break and make the load and the short circuits.
Audioscript_2: The line disconnector and the earthing switch are located in the lower part and insulated with SF6. The line disconnector is used to isolate busbar side from cable side, while the earthing switch is used to ground the cables side.
Audioscript_3: This combination of functions makes HySec an all-in-one apparatus.

## Slide 3: GSec
Upper part in epoxy resin and filled with SF6:
  compact design
  long-term protection against external environment
  Sealed for life: 30 years
Lower part in stainless steel
  Metallic partition (PM) between busbar and cable compartments
  Safety for operators during maintenance activities
Lower bushings with integrated capacitive dividers:
  Direct cable connection
Compact and safe structure
Notes: Audioscript: The upper shell of HySec is made of epoxy resin sealed for life with SF6 to provide a compact design and to provide long-term protection against external environment.
Audioscript_1: The lower shell is made of stainless steel to provide metallic partition between busbar and cable compartments which results in improved safety for operators performing maintenance on the panel.
Audioscript_2: The lower shell presents a safety valve on the rear part, which releases SF6 gas in case of accidental overpressure opposite to the front of the panel.
Audioscript_3: The combination of epoxy resin together with stainless steel makes HySec structure compact and safe.

## Slide 4: GSec
Line actuators:
Single spring mechanism (1S – dead centre)
Double spring mechanism (2S – stored energy)
Earth actuator:
Single spring mechanism (1S – dead centre)
Line operating slot
Earth operating slot
Line diagram with indicators
Pushbuttons (for 2S actuator)
Voltage indicators
Spring charged signal
Fuse blown signal
Actuators

## Slide 5: GSec
Actuators diagrams
1S – Single Spring | 2S – Double Spring
time
time
Actuation speed is independent from operator

## Slide 6: GSec
GSec/T1
1S – Single spring mechanism
Typical units
GSec/T2
2S – Double spring mechanism (stored energy)

## Slide 7: GSec
Typical units
GSec/IB
1S – Single spring mechanism
For panels with removable circuit breakers
Downstream earthing switch (interlocked)
GSec/T2F
2S – Double spring mechanism
Fuse tripping system
Fuse base
Fuse blown indicator
Downstream earthing switch (interlocked)

## Slide 8: GSec
Line disconnector - Earthing switch
  It is possible to close the earthing switch only if the line switch-disconnector is open
Earthing switch – Panel door
  It is possible to open the door only if the earthing switch is closed
Mechanical interlocks for safety
(1)
(2)
(3)
Closed
Open - Isolated
Earth
Notes: Audioscript: Several mechanical interlocks are integrated in HySec in order to prevent unsafe operations. The operating sequence can only follow the positions from 1 to 4 and from 4 to 1, without skipping anyone of them.
Audioscript_1: In particular, thanks to the interlock between the circuit breaker and the line disconnector, it is possible to close the breaker only if the disconnector is closed and it is possible to open the disconnector only if the breaker is open.
Audioscript_2: Additionally, thanks to the interlock between the line disconnector and the earthing switch, It is possible to close the earthing switch only if the disconnector is open.
Audioscript_3: Finally, thanks to the interlock between the earthing switch and the panel door, it is possible to open the door only if the earthing switch is closed.

## Slide 9: GSec
Wide range of accessories
Line Switch Disconnector
- Shunt opening release (T2/T2F)
- Shunt closing release (T2/T2F)
- Pushbutton protection (T2/T2F)
- Fuse blown contact (T2F)
- Motor closing spring charger
- Auxiliary contacts 4NC/4NO
- Key locks
- VPIS
- Manometer or pressure switch
Earthing switch
- Auxiliary contacts 4NC/4NO
- Key locks
Notes: Audioscript: HySec has the possibility to be equipped with a wide range of accessories, both for the circuit breaker part and the disconnector and earthing switch part.

## Slide 10: GSec
Safety and Compactness
Safety
- Metallic partition thanks to lower part in stainless steel - Mechanical interlocks to prevent unsafe operations - Separate operating seats for line and earth
Compactness
- Can fit 375mm wide panels - No need for cross-beam with insulators and direct cables connection thanks to integrated capacitive dividers

## Slide 11: GSec
Three positions load-break switch disconnector:
SF6 Load break switch
SF6 Disconnector
SF6 Earthing switch (cable side)
SF6 three-positions LBS
Rated Voltage [kV] | 12 (1S / 2S) | 17.5 (1S / 2S) | 24 (1S / 2S)
Rated Current [A] | 630 / 800 | 630 / 800 | 630
Short time current [kA] | 16(3s) / 25(2s) | 16(3s) / 20(3s) | 16(3s) / 20(2s)
Mechanical class | Line: M1 / M2 – Earth: M0 |  | 
Electrical class | Line: E3 – Earth: E2 |  | 
Notes: Audioscript: HySec is the first ABB multifunction apparatus integrating the functions of vacuum circuit breaker, SF6 line disconnector and SF6 earthing switch.
Audioscript_1: Its rated voltage is up to 24 kV, while its rated current is up to 600 A. Its breaking capacity is up to 16 kA, which is also its short time current withstand capability for 1 second.
Audioscript_2: HySec is able to perform 10.000 mechanical close-open operations. Its electrical life is classified as E2 and, up to 400 A, C2 for back to back capacitor switching.
Audioscript_3: HySec is also able to perform the fast operation cycle.