Author: S.Eichler
Company: E&H Mediendesign

Item	Qty	Description of products and services	Price per	Amount
			unit

		
		Blind/ Roller Shutter Actuator with Binary Inputs, 6f, 230 V AC, MDRC	Carry:

	For the control of up to 6 shutter or blind drives (230V) via KNX and 
	the connection of up to 12 potential free contacts.

	-	No additional power supply needed
	-	Electromechanically locked outputs for protection of the drives
	-	Ansteuerung einer Vorzugslage bei Busspannungsausfall

	Function: Positioning of
	-	Shutters / Blinds
	-	Awnings
	-	Ventilation damper
	-	Gates and windows

	Software functionality outputs:
	-	Cyclical monitoring
	-	Sending and switching delay after bus voltage recovery
	-	Request status values via object
	-	Limited number of telegrams
	-	Preferred position on bus voltage failure- and recovery
	-	Safety function (2 x wind alarm, rain alarm, frost alarm with cyclical monitoring, 
		block and forced operation) and reaction on reset of safety function
	-	Direct commands UP/DOWN, STOP/Slat Adjustment
	-	Move to position height/slat 0…255
	-	8-Bit scene
	-	Dead times of blind/shutter adjustable
	-	 Automatic sun protection (position height/slat at sun) and sun tracking
	-	Status messages: height/slat 0…255, upper/lower end position, 
		status information (2 Byte)
	-	Dead times of blind/shutter adjustable
	-	Switch mode with staircase lighting function
	A cascading of functions is possible.

	Software functionality inputs:
	-	Use as switch sensor
	-	Use as switching / dimming sensor
	-	Use as shutter / blind sensor
	-	Use for value sending / forced operation
	-	Blocking of inputs
	-	cyclical sending
	-	Minimum signal duration
	-	1 or 2 push button operating for shutters / blinds
	-	internal connection with outputs
	A cascading of functions is possible.

				JRAS_623031_AT_EN_V2-0
				2CDC506086D0201	Carry:

Item	Qty	Description of products and services	Price per	Amount
			unit

		
		Blind/ Roller Shutter Actuator with Binary Inputs, 6f, 230 V AC, MDRC	Carry:

	Outputs	6 indpenendent outputs
			(each channel 2 relay outputs UP / DOWN)

	Inputs	12 indpendant inputs, contact scanning

	Maximum power consumption device	4.8 W
	Maximum power consumption KNX	250 mW

	Operating voltage	max. 230 V AC, 45...65 Hz
	Rated current outputs	max. 6 A
	Operating voltage KNX	21 ... 30 V DC
	Scanning current / voltage inputs	0.1 mA/32 V

	Connection
		Load circuits	-	screw terminals with combination 
				head screws
			-	for cable 0,2 bis 6 mm²
		KNX	Screwless bus connection terminal

	Housing material	-	Plastic, halogen free
			-	Flammability V-0 as per UL94

	Type of protection	IP 20, EN 60 529

	Mounting	on 35 mm mounting rail, EN 60 715

	Mounting position	any

	Width	12 TE at 18 mm (216 mm)

	Manufacturer	ABB STOTZ-KONTAKT

	Type	JRA/S 6.230.3.1

	Material:..........	Labor:..........

				JRAS_623031_AT_EN_V2-0
				2CDC506086D0201	Carry: