## Type Test Report
V6.0.1 - 1.0.6304.21741
[5 empty] | Date of Issue: | 2017-05-24 09:54
Type Test Report
[5 empty] | Type: | M3JM 80MA 2
[5 empty] | Product Code: | 3GJM081310-_DH
[5 empty] | Protection type: | Ex d I Mb
[5 empty] | Cert. No.: | LCIE 11 A TEX 3086X /
IECEx LCI 04.0029X
Rating:
|  | V |  | Hz | kW | r/min | A | cos φ | Duty
3~Motor |  | 690 | Y | 50 | 0.75 | 2876 | 0.92 | 0.85 | S1
Ins. Class F |  | 400 | D | 50 | 0.75 | 2877 | 1.54 | 0.85 | S1
IP 66 |  | 415 | D | 50 | 0.75 | 2886 | 1.5 | 0.85 | S1
37 kg
Amb. -20°C...+40°C
50Hz: IE2-80.1%(100%)-79.5%(75%)-75.7%(50%)
Resistance |  |  |  |  | Insulation resistance at |  | 30 |  | Overload
Line |  | Ambient: | 21.5 | [5 empty] | Torque | 160 | 15
U1 - V1 | 13.453 |  |  |  | 24500 |  | 1000
U1 - W1 | 13.412
V1 - W1 | 13.457
[5 empty] | High-voltage test |  | 2918 |  | 1
Test | Torque | Line |  |  | Input |  | Output
| [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos φ | h [%]
No-load test |  | 400.3369 | D | 50.0132 | 0.81739 | 0.11204 |  |  | 0.19784
Locked-rotor test |  | 60.3979 | D | 50.0225 | 1.539 | 0.10452 |  |  | 0.64916
Thermal test (100% load) | 2.4953 | 399.9252 | D | 50.0132 | 1.6234 | 0.94521 | 0.75 | 2870.1748 | 0.8404 | 79.3472
Partial load points:
~75% load | 1.8488 | 399.9397 | D | 50.0132 | 1.3315 | 0.71995 | 0.5625 | 2905.3948 | 0.78042 | 78.1304
~50% load | 1.2192 | 399.9351 | D | 50.0132 | 1.0864 | 0.50707 | 0.375 | 2937.1235 | 0.67371 | 73.9537
~25% load | 0.60362 | 399.9278 | D | 50.0132 | 0.90556 | 0.30495 | 0.1875 | 2966.2761 | 0.48607 | 61.4845
Temperature rise at rated load. |  |  |  | [°C] | [K] | Method |  | Measurement method
|  | Stator winding : |  |  | 29.947 | 1 |  | 1 Resistance
|  | Frame : |  |  | 15.3569 | 2 |  | 2 Thermocouples
|  | Bearing D-end : |  |  | 23.5947 | 2 |  | 3 Thermometer
|  | Ambient Temperature : |  | 25 |  | 2
[9 empty] | Starting current (IS / IN) : | 7.3003
These tests have been carried out on motor no. 3G1F1643356089B, | [8 empty] | Locked rotor torque (TL / TN) : | 3.8476
on date 22.12.2016, which is identical in electrical design with the above.
Manufactured and tested in acc. to IEC/EN 60034-1:2010 and IEC/EN 60034-2-1:2014 Method 2-1-1B.
On behalf of customer
On behalf of manufacturer
Tested by ABB Oy, Motors and Generators, Vaasa, Finland
ISO/IEC 17025 certified laboratory | [5 empty] | Tommi Pantti, Test Floor Manager
|  | ABB, Motors and Generators | [5 empty] | Telephone | +358 10 2211
|  | www abb.com/motors&generators | [5 empty] | Telefax | +358 10 22 47372