## Type Test Report
V6.0.1 - 1.0.6358.18430
[5 empty] | Date of Issue: | 2017-06-27 07:48
Type Test Report
[5 empty] | Type: | M3GP 100LD 4
[5 empty] | Product Code: | 3GGP102324-B
[5 empty] | Protection type: | Ex tb IIIB T125C Db
[5 empty] | Cert. no.: | VTT 12 ATEX 051 X /
VTT 12.0010X
Rating:
|  | V |  | Hz | kW | r/min | A | cos φ | Duty
3~Motor |  | 690 | Y | 50 | 3 | 1450 | 3.54 | 0.79 | S1
Ins. Class F |  | 400 | D | 50 | 3 | 1450 | 6.1 | 0.79 | S1
IP 65 |  | 460 | D | 60 | 3 | 1755 | 5.42 | 0.78 | S1
38 kg
Amb. -20°C...+40°C
50Hz: IE2- 86.8%(100%)-86.9%(75%)-85.3%(50%)
60Hz: IE2- 87.6%(100%)
Resistance |  |  |  |  | Insulation resistance at |  | 40.5 |  | Overload
Line |  | Ambient: | 20 | [5 empty] | Torque | 160 | 15
U1 - V1 | 2.914 |  |  |  | 33000 |  | 1000
U1 - W1 | 2.913
V1 - W1 | 2.914
[5 empty] | High-voltage test |  | 2913 |  | 1
Test | Torque | Line |  |  | Input |  | Output
| [Nm] | U[V] |  | f[Hz] | I[A] | P1 [kW] | P2 [kW] | n[r/min] | cos φ | h [%]
No-load test |  | 400.2051 | D | 50.0127 | 3.3062 | 0.22122 |  |  | 0.096578
Locked-rotor test |  | 69.0688 | D | 50.0005 | 6.1024 | 0.40248 |  |  | 0.55132
Thermal test (100% load) | 19.8038 | 399.8872 | D | 50.0127 | 6.266 | 3.5191 | 3 | 1446.5838 | 0.81062 | 85.2499
Partial load points:
~75% load | 14.7026 | 399.8643 | D | 50.0127 | 5.123 | 2.6329 | 2.25 | 1461.3734 | 0.7418 | 85.4573
~50% load | 9.7107 | 399.8758 | D | 50.0127 | 4.1847 | 1.7918 | 1.5 | 1475.064 | 0.61801 | 83.7165
~25% load | 4.8146 | 399.9095 | D | 50.0127 | 3.5389 | 0.99094 | 0.75 | 1487.5592 | 0.40416 | 75.6854
Temperature rise at rated load. |  |  |  | [°C] | [K] | Method |  | Measurement method
|  | Stator winding : |  |  | 47.4977 | 1 |  | 1 Resistance
|  | Frame : |  |  | 20.626 | 2 |  | 2 Thermocouples
|  | Bearing D-end : |  |  | 19.3052 | 2 |  | 3 Thermometer
|  | Ambient Temperature : |  | 25 |  | 2
[9 empty] | Starting current (IS / IN) : | 7.8754
These tests have been carried out on motor no. 3G1F1702384138B, | [8 empty] | Locked rotor torque (TL / TN) : | 3.0959
on date 08.02.2017, which is identical in electrical design with the above.
Manufactured and tested in acc. to IEC/EN 60034-1:2010 and IEC/EN 60034-2-1:2014 Method 2-1-1B.
On behalf of customer
On behalf of manufacturer
Tested by ABB Oy, Motors and Generators, Vaasa, Finland
ISO/IEC 17025 certified laboratory | [5 empty] | Tommi Pantti, Test Floor Manager
|  | ABB, Motors and Generators | [5 empty] | Telephone | +358 10 2211
|  | www abb.com/motors&generators | [5 empty] | Telefax | +358 10 22 47372