## Instructions
LV Drives Harmonic Estimator Instructions | [7 empty] | REV: | 220705P
The following instructions describe the data needed to perform an harmonic estimate of a drive system.
Key to cell color on Input tab
Cell for data input (not locked)
Cell with calculated data (locked)
Cell with data or text (locked)
Cell with drop-down selection
Cell that is disabled
Cell with an issue
Utility Input Power Instructions
Step #
1 | In cell J4, enter the System Freq [Hz]. Typically this would be 60.
2 | In cell H4, select "UTILITY" as the power source from the drop-down.
3 | In cell H5, enter the Utility [V] voltage feeding the transformer primary that supplies the voltage to the drives.
If you don't know the value, use 13800 as a default.
4a | For cell H6, if you know the MVAsc feeding the transformer, enter it.
4b |  | If you don't know the value, use 400 as a default.
4c |  | If you are given the positive sequence R and X values, enter them into cells M24 and M25 respectively.
The value found in cell M30 should then be entered in to H6.
4d |  | If you are given the symmetrical Isc value, enter it into cell M34.
The value found in cell M37 should then be entered into H6.
See the "Worksheets Notes" section below for more information.
5 | In cell H7, if there is an ID Tag number for the transformer, enter that. If not, you may leave this blank.
6 | In cell H8, enter the kVA rating of the transfomrer. If the transformer has multiple kVA ratings, use the smallest value.
7 | In cell H9, enter the secondary voltage of the transformer.
8 | In cell H10, enter the %Z of the transformer. This is usually noted on the transformer nameplate or from
a one-line diagram. If unknown, use 5.75 as a default.
9 | In cell H12, you can select either "XFMR Pri" or "XFMR Sec" as the PCC location for TDD calculations from the drop-down.
IEEE 519-2014 specifies the primary side of the transformer, which is the default.
The voltage distortion will be at the transformer secondary as noted in H11.
Generator Input Power Instructions
Step #
1 | In cell J4, enter the System Freq [Hz]. Typically this would be 60.
2 | In cell H4, select "GENERATOR" as the power source from the drop-down.
3 | In cell J5, if there is an ID Tag number for the generator enter that. If not, you may leave this blank.
4 | In cell J6, enter the kW rating of the generator.
5 | In cell J7, enter the power factor rating of the generator. The default is 0.8.
Cell J8 calculates the rated kVA of the generator, which is the kW rating / PF rating = (J6/J7)
6 | In cell J9, enter the secondary voltage of the generator.
7 | In cell J10, enter the Sub-Transient Reactance of the generator, also given as Xd".
This information should be available from the generator data sheet.
Cell J12 states that the location of the PCC will be at the generator bus.
The voltage distortion will also be at the generator bus.
NOTE:
If a generator is feeding the drives through a transformer, the generator becomes the utility.
First enter the generator information in cells J4, J5, J6, J7, J9, J10.
Then follow the instructions for Utility Input Power (B13 above).
Utility [V] would be the generator voltage.
|  | Utility [MVAsc} would be the generator kVA/1000/Xd" = |  |  | 12.5 | (from Input cell O8)
Enter the information for the transformer and max loading as requested.
Linear Load Notes
When the UTILITY is selected, and the Linear Load Selection is "Max Percent of Source", you will see this:
When the GENERATOR is selected, and the Linear Load Selection is "Max Percent of Source", you will see this:
Linear loads can be added in two ways.
Cell F14 allows you to select either "Max Percent of Source" or "Itemized".
The red triangles in the upper right-hand corners indicates that there are notes for the cell.
Simply hover over the cell with your cursor to see the notes.
Max Percent of Source is where you enter the maximum % loading you expect the transformer to be loaded to (if source is Utility).
Or, if the source is Generator, you enter the maximum % loading you expect the generator to be loaded to.
You may also specify the Power Factor of this linear load.
As you change the number of drives, the program will change the linear load in order to maintain the % value entered.
If the drive loads causes the % load entered to be exceeded, this will turn red and a design check message will appear.
When either UTILITY or GENERATOR is selected, and the Linear Load Selection is "Itemized", you will see this:
Itemized is where you enter specific values for linear loads and their average PF.
A total HP motor load value, with its average PF
A total kW resistive load value, with a fixed PF of 1.00
A total kVA load value, with its average PF
A total A load value, with its average PF
As you change the number of drives, the program will add these linear loads to the drive loads, so the total loading on the transformer or
generator will also change.
If the drive or linear loads cause the loading on the transformer or generator to exceed its rating, a design check message will appear
and the cells in jeopardy will turn red.
Variable Frequency Drive List
Step #
1 | In cell C26, if there is an ID Tag number for the drive you are entering, place it here.
It could also refer to a group of like drives (same drive type and filter).
For that, sum the HP ratings and enter that value.
2 | In cell F26, select the drive type from the drop-down list.
The drive types that are available are:
6 Pulse w/ No Impedance
6 Pulse w/ 3% Impedance
6 Pulse w/ 5% Impedance
12 Pulse Drive
18 Pulse Drive
ULH (AFE) Drive
3 | In cell G26, if there is or needs to be an additional filter on the input of the drive,
select the filter type from the drop-down list.
The types of filters that are available are:
none (leave the cell blank or delete the filter that was selected)
1.5% AC Reactor
2.5% AC Reactor
3% AC Reactor
5% AC Reactor
7% AC Reactor
10% AC Reactor
7% THDi Passive Filter
5% THDi Passive Filter
If a drive/filter combination is not allowed, the cell will turn red
See the setion "Drive/Filter Combinations Not Allowed" below for that list
You can copy and paste drives and filters using "Paste Special", "Values". Do not use a simple paste function.
4 | In cell H26, enter the HP rating of the drive.
If there are multiple drives of the same type, they can be grouped as one entry
and the total rated HP would be the value in this cell.
5 | In cell I26, enter the % Load at which the drive will operate.
The default value is 100%.
6 | In cell J26, enter the length of cable, in feet, between the transformer and drive input.
The default value is 32.8 feet (10 meters).
This default value can be changed in the Adjustable Program Constants table below.
If multiple drives are entered on a line, use an average of the cable lengths.
7 | Continue with the cells in rows 27 through 75 (max of 50 entries).
Cell H76 is the sum of the values in the Rated HP column
When doing any "Cut and Paste", be sure to paste "Values (V)", otherwise things get messed up!
Adjustable Program Constants
This program uses the following constants for various parameters.
If needed, you may change the values within these grey cells to more closely match the estimate to your system.
|  | Parameter | Entered Value |  | Default
|  | motor efficiency [pu] | 0.95 |  | 0.95
|  | drive efficiency [pu] | 0.97 |  | 0.97
|  | input cable [ft] | 32.8 |  | 32.8
|  | cable inductance [uH/m] | 0.435 |  | 0.435
|  | xfmr has delta winding [Y/N] | Y |  | Y | If no delta winding, enter N
|  | 7% THDi Filter, no load amps | -35 | A @ 100hp | -35 |  | Leading PF Current
|  | 5% THDi Filter, no load amps | -40 | A @ 100hp | -40 |  | Leading PF Current
Drive/Filter Combinations Not Allowed
The following Drive/Filter combinations are not considered to be realistic drive systems,
and are not implemented. If selected, an "X" will show up in Column A of the Input sheet (col C on this sheet),
and the filter and HP cells will turn red.
|  | Drive | Filter
| X | 12 Pulse Drive | 1.5% AC Reactor
| X | 12 Pulse Drive | 2.5% AC Reactor
| X | 12 Pulse Drive | 3% AC Reactor
| X | 12 Pulse Drive | 5% AC Reactor
| X | 12 Pulse Drive | 7% AC Reactor
| X | 12 Pulse Drive | 10% AC Reactor
| X | 12 Pulse Drive | 7% THDi Passive Filter
| X | 12 Pulse Drive | 5% THDi Passive Filter
| X | 18 Pulse Drive | 1.5% AC Reactor
| X | 18 Pulse Drive | 2.5% AC Reactor
| X | 18 Pulse Drive | 3% AC Reactor
| X | 18 Pulse Drive | 5% AC Reactor
| X | 18 Pulse Drive | 7% AC Reactor
| X | 18 Pulse Drive | 10% AC Reactor
| X | 18 Pulse Drive | 7% THDi Passive Filter
| X | 18 Pulse Drive | 5% THDi Passive Filter
| X | ACS800/ACH580 ULH (AFE) | 1.5% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 2.5% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 3% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 5% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 7% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 10% AC Reactor
| X | ACS800/ACH580 ULH (AFE) | 7% THDi Passive Filter
| X | ACS800/ACH580 ULH (AFE) | 5% THDi Passive Filter
Quick View Notes
The top left box provides background information on the
Short-circuit current (Isc) and the short-circuit MVA (MVAsc) available at the
Input and the output of the transformer when "UTILITY" is selected.
Or, it will show the Isc and MVAsc at the output of the generator when
"GENERATOR" is selected.
The "Design Checks:" would show the following if true:
•Total kVA load exceeds the MAX % kVA loading!
•Total kVA load exceeds the Transformer kVA rating!
•Total kW load exceeds the MAX % kW loading!
•Total kW load exceeds the Generator kW rating!
•Total kVA load exceeds the Generator kVA rating!
If the kVA or kW rating is exceeded, the design check shows up and the appropriate cells turn red.
If there are no issues with the Design Checks, the "No power limits exceeded" message would show.
The middle box on the left shows various system parameters and the TDD pass/fail.
The middle box on the right gives various current values regarding the drive(s) and the linear load.
These currents are on the secondary of the transformer when the source is the UTILITY,
or between the loads and the generator when the source is the GENERATOR.
Power values and totals are also given.
Please note that the Total kVA is not the sum of the individual kVA values.
The kW values (P) are summed.
The kVAR values (Q) are summed.
The distortion kVAR values (D) are summed.
Those are then vectorially summed to give a total kVA value (S).
S = sqrt(P^2 + Q^2 + D^2)
The % of Rated shows the % loading on the XFMR or GEN based on its rating.
Worksheets Notes
The top two boxes are used to convert various parameters into MVAsc values
at the transformer primary.
The bottom box is used to convert various parameters into Rated HP values
for the drive ratings.
Report
The "Report" tab provides a summary of the results than can be printed as a PDF.
Page 1 is a summary including the Harmonic Results
Page 2 is a listing of the drives that were considered in the system
Page 3 shows graphs of the current and voltage harmonic spectrums
Page 4 tabulates the current and voltage harmonic distortion as raw values and as percentages of the fundamental value.
An "x" in the column to the right of the "IEEE TDD Limit [%]" column indicates that the value of the calculated
system current distortion for that particular harmonic number exceeds the recommended limit found in
IEEE 519-2014 Table 2.
Any of the pages can be printed to the "Adobe PDF" printer that will create a PDF
file that can then be shared with a customer or user.
Use the following setup:
Print Active Sheets
Portrait Orientation
Letter: 8.5" x 11"
Normal Margins
|  | Top 0.75" | Bottom 0.75"
|  | Left 0.7" | Right 0.7"
|  | Header 0.3" | Footer 0.3"
Custom Scaling
Page Setup: Adjust to 60% Normal Size
Qual Notes
The "Qual Notes" tab is where you can modify or re-word the qualifications
seen at the bottom of the "Harmonic Estimation Summary Report" sheet 1.
In the future, this tab can be hidden with a password chosen by you.
The following describes how you can use these notes:
1) On the Report tab, page 1, the first 6 rows of notes (rows 48-59)are selected from the drop-down menus.
a. They come from the Qual Notes tab, rows 3-15.
b. That is why they are colored light orange.
2) On the Report tab, page 1, the next 4 rows of notes are there for notes you may want to type in that would be unique for that particular order.
a. They would not be used for notes that are unique for you that you may use on multiple analyses.
b. That is why they are colored light gray.
3) On the Qual Notes tab, if there are notes that you want to use on multiple orders, you would put those notes into rows 11-15 of the Qual Notes tab.
a. Those rows are presently named, “Special Note 1”, “Special Note 2”, etc.
b. You can change their names to whatever you like in column B
c. You can customize a note that you will use often in column C
d. You can then select that note from the drop down in rows 48-59 of the Report tab.
Analysis Notes
Please be aware of the following anomaly when performing harmonic estimates using a mix of different Drive/Filter combinations.
1) The harmonics created by each Drive/Filter combination are summed as noted in IEEE Std 399-1997, 10.2, using the principle of superposition
2) This is a conservative method of determining the total harmonics in a system
3) In reality, some of the higher harmonics will partially cancel when summed due to the phase angle magnitude of a particular harmonic
between different Drive/Filter combinations
4) A result of this difference between how this estimator sums harmonics and what happens in reality, the estimator may indicate
a slightly higher harmonic magnitude than what would be expected
Method of Harmonic Estimation
The method used in this harmonic estimator tool is with tables of harmonics for each type of Drive/Filter combination, at various Rsc ratios.
The Drive/Filter combinations are represented by a typical set of components that are linearly scaled for the HP rating.
These tables were created using simulation tools such as Pspice and ANSYS Simplorer, and were verified with actual measurements.
Questions or Support?
For questions or support, please contact ABB at:
ABB HVAC Applications Group
1-800-752-0696
us-hvacappeng@abb.com

## Input
[6 empty] | REV: | 220705P
|  | Harmonic Estimation Data Input |  |  |  | 2022-07-05
Quick View
Project ID: |  |  |  | Source Selected | UTILITY | System Freq [Hz] | 60
Revision: |  |  |  | Utility [V] | 13800 | Generator ID Tag |  |  | Utility Feed | XFMR Sec | GEN Bus | Design Checks: | No power limits exceeded
Date: |  |  |  | Utility [MVAsc] | 400 | Rated Power [kW] | 2000
Project Name: |  |  |  | Transformer ID Tag |  | Power Factor | 0.8 | Isc [kA] | 16.7348 | 38.49 | 15.0352
Contact: |  |  |  | Rated kVA [kVA] | 2000 | Apparent Power [kVA] | 2500 | MVAsc | 400 | 32 | 12.5
Contact Email: |  |  |  | Secondary Voltage [V] | 480 | Output Voltage [V] | 480
Created by: |  |  |  | Impedance [% Z] | 5.75 | Sub-Transient Reactance [Xd"] | 0.2
Created by Email: |  |  |  | PCC for Vthd | XFMR Sec |  |  |  | Value |  |  | Load | Amps | kVA | kW | PF
Notes: |  |  |  | PCC for TDD | XFMR Pri | PCC for TDD | GEN Bus | Isc/Iload | 285.7143 |  |  | Drives, harm | 0
[8 empty] | TDD Limit [%] | 15 |  |  | Drives, fund | 0
|  | Linear Load Selection | Max Percent of Source |  |  |  |  | TDD [%] | 0 |  |  | Drives, total | 0 | 0 | 0 | 1
|  | Max Percent of Source | [5 empty] | TDD OK? | PASS |  |  | Linear, total | 1683.9383 | 1400 | 1260 | 0.9
|  | MAX % kVA loading of Transformer |  | 70 | % | 0.9 | avg PF | vTHD [%] | 0 |  |  | Total | 1683.9383 | 1400 | 1260 | 0.9
|  |  |  | 100 |  | 0.9 | [5 empty] | % of Rated | 70 | 70
Itemized
|  | Total HP motor loads |  | 0 | HP | 0.85 | avg PF |  |  |  |  | See Instructions tab, line 283, note regarding Total [kVA]
|  | Total kW resistive loads |  | 0 | kW | 1 | PF
|  | Total kVA loads |  | 0 | kVA | 0.9 | avg PF
|  | Total A loads |  | 0 | A | 0.9 | avg PF
Worksheets
VFD # | ID Tag |  | Drive | Additional Filter | Rated HP | % Load | Input cable, ft
1 | [5 empty] | 100% |  | Determine Utility [MVAsc] from R and X
2 | [5 empty] | 100% |  | R = | 0.023 | Ohms
3 | [5 empty] | 100% |  | X = | 0.48 | Ohms
4 | [5 empty] | 100% |  | X/R = | 20.8696
5 | [5 empty] | 100% |  | Z = | 0.48055 | Ohms
6 | [5 empty] | 100% |  | Utility [V] = | 13800 | Volts | (from cell H5)
7 | [5 empty] | 100% |  | Isc = | 16579.7975 | Amps
8 | [5 empty] | 100% |  | MVAsc = | 396.2953 | MVA
9 | [5 empty] | 100% |  |  | enter this value into "Utility [MVAsc]" cell H6
10 | [5 empty] | 100%
11 | [5 empty] | 100% |  | Determine Utility [MVAsc] from Positive Sequence Isc at xfmr primary
12 | [5 empty] | 100% |  | Isc = | 5000 | A
13 | [5 empty] | 100%
14 | [5 empty] | 100% |  | Utility [V] = | 13800 | Volts | (from cell H5)
15 | [5 empty] | 100% |  | MVAsc = | 119.5115 | MVA
16 | [5 empty] | 100% |  |  | enter this value into "Utility [MVAsc]" cell H6
17 | [5 empty] | 100%
18 | [5 empty] | 100% |  | Determine Rated HP from Motor kW
19 | [5 empty] | 100% |  | Motor kW = | 100 | kW
20 | [5 empty] | 100% |  | Rated HP = | 134.0483 | HP
21 | [5 empty] | 100%
22 | [5 empty] | 100% |  | Determine Rated HP from Motor V, FLA, eff, pf
23 | [5 empty] | 100% |  | Motor V = | 460 | V | Motor eff = | 0.95
24 | [5 empty] | 100% |  | Motor FLA = | 124 | A | Motor pf = | 0.84
25 | [5 empty] | 100% |  | Rated HP = | 105.6828 | HP
26 | [5 empty] | 100%
27 | [5 empty] | 100%
28 | [5 empty] | 100%
29 | [5 empty] | 100%
30 | [5 empty] | 100% |  | Color Key
31 | [5 empty] | 100%
32 | [5 empty] | 100% |  |  | Cell for data input (not locked)
33 | [5 empty] | 100% |  |  | Cell with calculated data (locked)
34 | [5 empty] | 100% |  |  | Cell with data or text (locked)
35 | [5 empty] | 100% |  |  | Cell with drop-down selection
36 | [5 empty] | 100% |  |  | Cell that is disabled
37 | [5 empty] | 100% |  |  | Cell with an issue
38 | [5 empty] | 100%
39 | [5 empty] | 100% |  | Column A
40 | [5 empty] | 100% |  | X | No Harmonic Data: Non-realistic Drive/Filter combination
41 | [5 empty] | 100%
42 | [5 empty] | 100%
43 | [5 empty] | 100%
44 | [5 empty] | 100%
45 | [5 empty] | 100%
46 | [5 empty] | 100%
47 | [5 empty] | 100%
48 | [5 empty] | 100%
49 | [5 empty] | 100%
50 | [5 empty] | 100%
|  |  |  | Total HP = | 0
Note on E15: Max Percent of Source This is a method to add an amount of linear loading to the drive loads in order to achieve the specified % load on the transformer or generator source. Typical values are 70% for the transformer loading, or 100% for the generator loading. The average Power Factor of this linear load can also be specified. Note that as the drive load changes, the amount of linear load will also change in order to maintain the % value specified. Note that changes to the avg PF cell I16 will have an effect on the total linear load amps in cell Q15, but the percentage of transformer maximum loading is still constant based on cell G16, so no changes to TDD% in cell M14 will occur.
Note on E18: Itemized This is a method to add specific linear loads to the drive loads on the system. The loads can be made up of motors where you specify the HP ratings and average PF, resistive loads where you specify the kW and the PF is fixed at 1.0,, kVA loads where you specify the average PF, or amp loads, again where you specify the average PF. As the drive loads chanage, these loads will stay the same.

## Report
0
|  |  | Harmonic Estimation Summary Report / 1 | [7 empty] | 2022-07-05 |  |  |  |  | Harmonic Estimation Summary Report / 2 |  |  |  | 2022-07-05 |  | Harmonic Estimation Summary Report / 3 | 2022-07-05 |  | Harmonic Estimation Summary Report / 4 | [6 empty] | 2022-07-05
[12 empty] | REV: | 220705P
| Project ID: | [12 empty] | Project ID: | [6 empty] | Project ID: |  |  | Project ID:
Revision:
Date:
Project Name:
| Contact: | [12 empty] | VFD # | ID Tag |  | Drive | Additional Filter | Rated HP | % Load
| Contact Email: | [12 empty] | 1 | [5 empty] | 100%
| Created by: | [12 empty] | 2 | [5 empty] | 100%
| Created by Email: | [12 empty] | 3 | [5 empty] | 100%
| Notes: | [12 empty] | 4 | [5 empty] | 100%
[14 empty] | 5 | [5 empty] | 100% |  |  |  |  | h | Current [A] | Ih [%] | IEEE TDD Limits [%] |  | Voltage[V] | Vh [%]
| Source Details |  |  |  | UTILITY Source Diagram | [8 empty] | 6 | [5 empty] | 100%
| Source Selected |  | UTILITY | [10 empty] | 7 | [5 empty] | 100% |  |  |  |  | 1 | 58.5718 | 100 | 100 |  | 480 | 100
| System Freq [Hz] |  | 60 | [10 empty] | 8 | [5 empty] | 100% |  |  |  |  | 2 | 0 | 0 | 3 |  | 0 | 0
| Utility [V] |  | 13800 | [7 empty] | AC Drives |  |  | 9 | [5 empty] | 100% |  |  |  |  | 3 | 0 | 0 | 12 |  | 0 | 0
| Utility [MVAsc] |  | 400 | [10 empty] | 10 | [5 empty] | 100% |  |  |  |  | 4 | 0 | 0 | 3 |  | 0 | 0
| Transformer ID Tag | [12 empty] | 11 | [5 empty] | 100% |  |  |  |  | 5 | 0 | 0 | 12 |  | 0 | 0
| Rated kVA [kVA] |  | 2000 | [10 empty] | 12 | [5 empty] | 100% |  |  |  |  | 6 | 0 | 0 | 3 |  | 0 | 0
| Secondary Voltage [V] |  | 480 | [10 empty] | 13 | [5 empty] | 100% |  |  |  |  | 7 | 0 | 0 | 12 |  | 0 | 0
| Impedance [% Z] |  | 5.75 |  | Utility |  |  | Transformer |  |  | Drive System |  |  | 14 | [5 empty] | 100% |  |  |  |  | 8 | 0 | 0 | 3 |  | 0 | 0
[14 empty] | 15 | [5 empty] | 100% |  |  |  |  | 9 | 0 | 0 | 12 |  | 0 | 0
[6 empty] | XFMR Pri |  |  | XFMR Sec |  | Linear Loads |  |  | 16 | [5 empty] | 100% |  |  |  |  | 10 | 0 | 0 | 3 |  | 0 | 0
| PCC for Vthd |  | XFMR Sec | [10 empty] | 17 | [5 empty] | 100% |  |  |  |  | 11 | 0 | 0 | 5.5 |  | 0 | 0
| MVAsc at PCC |  | 400 | [10 empty] | 18 | [5 empty] | 100% |  |  |  |  | 12 | 0 | 0 | 1.375 |  | 0 | 0
| Isc at PCC [kA] |  | 16.7348 | [10 empty] | 19 | [5 empty] | 100% |  |  |  |  | 13 | 0 | 0 | 5.5 |  | 0 | 0
[14 empty] | 20 | [5 empty] | 100% |  |  |  |  | 14 | 0 | 0 | 1.375 |  | 0 | 0
[14 empty] | 21 | [5 empty] | 100% |  |  |  |  | 15 | 0 | 0 | 5.5 |  | 0 | 0
| Load Details | [5 empty] | Design Checks | [6 empty] | 22 | [5 empty] | 100% |  |  |  |  | 16 | 0 | 0 | 1.375 |  | 0 | 0
| Linear Loads |  | Load | PF |  |  | No power limits exceeded | [6 empty] | 23 | [5 empty] | 100% |  |  |  |  | 17 | 0 | 0 | 5 |  | 0 | 0
| Total HP motor loads [hp] |  | 0 | 0.85 | [9 empty] | 24 | [5 empty] | 100% |  |  |  |  | 18 | 0 | 0 | 1.25 |  | 0 | 0
| Total kW resistive loads [kW] |  | 0 | 1 | [9 empty] | 25 | [5 empty] | 100% |  |  |  |  | 19 | 0 | 0 | 5 |  | 0 | 0
| Total kVA loads [kVA] |  | 0 | 0.9 | [9 empty] | 26 | [5 empty] | 100% |  |  |  |  | 20 | 0 | 0 | 1.25 |  | 0 | 0
| Total ampere loads [A] |  | 0 | 0.9 | kVA | [8 empty] | 27 | [5 empty] | 100% |  |  |  |  | 21 | 0 | 0 | 5 |  | 0 | 0
| MAX % kVA loading of xfmr [%] |  | 70 | 0.9 | 1400 | [8 empty] | 28 | [5 empty] | 100% |  |  |  |  | 22 | 0 | 0 | 1.25 |  | 0 | 0
[14 empty] | 29 | [5 empty] | 100% |  |  |  |  | 23 | 0 | 0 | 2 |  | 0 | 0
|  | kVA | % rated kVA | kW | Amps | [8 empty] | 30 | [5 empty] | 100% |  |  |  |  | 24 | 0 | 0 | 0.5 |  | 0 | 0
| Total Load at PCC | 1400 | 70 | 1260 | 58.5718 | [8 empty] | 31 | [5 empty] | 100% |  |  |  |  | 25 | 0 | 0 | 2 |  | 0 | 0
[14 empty] | 32 | [5 empty] | 100% |  |  |  |  | 26 | 0 | 0 | 0.5 |  | 0 | 0
| Harmonic System Details |  |  | Harmonic Results | [9 empty] | 33 | [5 empty] | 100% |  |  |  |  | 27 | 0 | 0 | 2 |  | 0 | 0
|  |  |  | RESULTS | [5 empty] | ABB is pleased to inform you that the harmonic analysis shows that the system meets the IEEE 519-2014 Total Demand Distortion (TDD) limit at the PCC. |  |  |  | 34 | [5 empty] | 100% |  |  |  |  | 28 | 0 | 0 | 0.5 |  | 0 | 0
[14 empty] | 35 | [5 empty] | 100% |  |  |  |  | 29 | 0 | 0 | 2 |  | 0 | 0
| PCC location for TDD |  | XFMR Primary | The Total Demand Distortion (TDD CURRENT) is |  |  |  |  | 0% |  |  |  |  | 36 | [5 empty] | 100% |  |  |  |  | 30 | 0 | 0 | 0.5 |  | 0 | 0
[14 empty] | 37 | [5 empty] | 100% |  |  |  |  | 31 | 0 | 0 | 2 |  | 0 | 0
| Isc / I_load at PCC |  | 285.7143 | For this system, IEEE 519 allows TDD CURRENT up to |  |  |  |  | 15% |  |  |  |  | 38 | [5 empty] | 100% |  |  |  |  | 32 | 0 | 0 | 0.5 |  | 0 | 0
[14 empty] | 39 | [5 empty] | 100% |  |  |  |  | 33 | 0 | 0 | 2 |  | 0 | 0
| Location for vTHD |  | XFMR Secondary | The Total Harmonic Distortion (VOLTAGE) is |  |  |  |  | 0% |  |  |  |  | 40 | [5 empty] | 100% |  |  |  |  | 34 | 0 | 0 | 0.5 |  | 0 | 0
[14 empty] | 41 | [5 empty] | 100% |  |  |  |  | 35 | 0 | 0 | 1 |  | 0 | 0
[14 empty] | 42 | [5 empty] | 100% |  |  |  |  | 36 | 0 | 0 | 0.25 |  | 0 | 0
[14 empty] | 43 | [5 empty] | 100% |  |  |  |  | 37 | 0 | 0 | 1 |  | 0 | 0
| Qualifying Statements and Notes | [12 empty] | 44 | [5 empty] | 100% |  |  |  |  | 38 | 0 | 0 | 0.25 |  | 0 | 0
| Drives Listed | Harmonic analysis only includes the drives that are listed on page 2 of this report. | [11 empty] | 45 | [5 empty] | 100% |  |  |  |  | 39 | 0 | 0 | 1 |  | 0 | 0
[14 empty] | 46 | [5 empty] | 100% |  |  |  |  | 40 | 0 | 0 | 0.25 |  | 0 | 0
| Linear Load | All non-drive loading is assumed to be linear loading. | [11 empty] | 47 | [5 empty] | 100% |  |  |  |  | 41 | 0 | 0 | 1 |  | 0 | 0
[14 empty] | 48 | [5 empty] | 100% |  |  |  |  | 42 | 0 | 0 | 0.25 |  | 0 | 0
| 70% Load | Harmonic analysis assumes the MV to LV step down transformer is 70% loaded under peak loading. | [11 empty] | 49 | [5 empty] | 100% |  |  |  |  | 43 | 0 | 0 | 1 |  | 0 | 0
[14 empty] | 50 | [5 empty] | 100% |  |  |  |  | 44 | 0 | 0 | 0.25 |  | 0 | 0
| PCC IEEE-2014 | The point of common coupling (PCC) was chosen based on IEEE 519-2014. The TDD (current) was calculated on the primary (utility) side of the transformer. The vTHD (voltage), while not included in IEEE 519-2014, was calculated on the secondary (facility) side of the transformer. | [15 empty] | Total HP = | 0 | [5 empty] | 45 | 0 | 0 | 1 |  | 0 | 0
[25 empty] | 46 | 0 | 0 | 0.25 |  | 0 | 0
[25 empty] | 47 | 0 | 0 | 1 |  | 0 | 0
[25 empty] | 48 | 0 | 0 | 0.25 |  | 0 | 0
[25 empty] | 49 | 0 | 0 | 1 |  | 0 | 0
[25 empty] | 50 | 0 | 0 | 0.25 |  | 0 | 0
[25 empty] | Harmonic [A] | 0 | Arms |  | Harmonic [V] | 0 | Vrms
[25 empty] | Fund [A] | 58.5718 | Arms |  | Fund [V] | 480 | Vrms
[25 empty] | TDD [%] | 0 |  |  | vTHD [%] | 0
Please note that the information shown here is typical and does not constitute any guarantee of performance or measurement. Several outside factors can influence the harmonics measured on a power system, including other equipment within the plant and other equipment in neighboring plants. This can include, but is not limited to - drives, varying loads and/or other factory equipment. The calculated current and voltage harmonics shown in this report are for estimation purposes only.
M

## Qual Notes
Qualification Selections and Notes
5.75% Z | Harmonic analysis assumes the MV to LV step down transformer impedance to be approximately 5.75%
70% Load | Harmonic analysis assumes the MV to LV step down transformer is 70% loaded under peak loading.
80% Load | Harmonic analysis assumes the MV to LV step down transformer is 80% loaded under peak loading.
Drives Listed | Harmonic analysis only includes the drives that are listed on page 2 of this report.
Linear Load | All non-drive loading is assumed to be linear loading.
No Assumptions | There were no assumptions made, as all required information was provided to ABB
PCC IEEE-2014 | The point of common coupling (PCC) was chosen based on IEEE 519-2014. The TDD (current) was calculated on the primary (utility) side of the transformer. The vTHD (voltage), while not included in IEEE 519-2014, was calculated on the secondary (facility) side of the transformer.
Generator Back-Up | The point of common coupling (PCC) was chosen to be the generator bus, with 100% loading on the generator and a max TDD of 5%.
Special Note 1 | My unique set of notes.
Special Note 2
Special Note 3
Special Note 4
Special Note 5
ABB is pleased to inform you that the harmonic analysis shows that the system meets the IEEE 519-2014 Total Demand Distortion (TDD) limit at the PCC.
This particular combination of types of drives and filters does not meet the IEEE 519-2014 TDD Limit at the PCC. Please consult your local ABB representative to discuss this report.

## Drives (hidden)
Drive Loading Details
[18 empty] | TOTALS |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | at the drive
Per Unit
VFD # | Drive | Additional Filter | Drive Type | Filter Type | Drive/Filter Type | Rated HP | % Load | actual HP | Input cable, ft |  | Drive Selection |  | Filter Selection |  |  | A00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
1 | [5 empty] | 0 | 1 | 0 | 32.8 |  | 6 Pulse w/ No Impedance | A | none | 01 |  | A01 |  | 6 Pulse w/ No Impedance | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A01 | 0 | 0 | 0.995 | 0 | 0 | 0 | A01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
2 | [5 empty] | 0 | 1 | 0 | 32.8 |  | 6 Pulse w/ 3% Impedance | B | 1.5% AC Reactor | 02 |  | A02 |  | 6 Pulse w/ No Impedance | 1.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A02 | 0 | 0 | 0.967 | 0 | 0 | 0 | A02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A02 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 1.5026
3 | [5 empty] | 0 | 1 | 0 | 32.8 |  | 6 Pulse w/ 5% Impedance | C | 2.5% AC Reactor | 03 |  | A03 |  | 6 Pulse w/ No Impedance | 2.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A03 | 0 | 0 | 0.971 | 0 | 0 | 0 | A03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A03 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 2.5026
4 | [5 empty] | 0 | 1 | 0 | 32.8 |  | 12 Pulse Drive | D | 3% AC Reactor | 04 |  | A04 |  | 6 Pulse w/ No Impedance | 3% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A04 | 0 | 0 | 0.971 | 0 | 0 | 0 | A04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A04 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 3.0026
5 | [5 empty] | 0 | 1 | 0 | 32.8 |  | 18 Pulse Drive | E | 5% AC Reactor | 05 |  | A05 |  | 6 Pulse w/ No Impedance | 5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A05 | 0 | 0 | 0.966 | 0 | 0 | 0 | A05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A05 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 5.0026
6 | [5 empty] | 0 | 1 | 0 | 32.8 |  | ULH (AFE) Drive | F | 7% AC Reactor | 06 |  | A06 |  | 6 Pulse w/ No Impedance | 7% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A06 | 0 | 0 | 0.959 | 0 | 0 | 0 | A06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A06 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 7.0026
7 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Custom System | G | 10% AC Reactor | 07 |  | A07 |  | 6 Pulse w/ No Impedance | 10% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A07 | 0 | 0 | 0.949 | 0 | 0 | 0 | A07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A07 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 10.0026
8 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | 7% THDi Passive Filter | 08 |  | A08 |  | 6 Pulse w/ No Impedance | 7% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A08 | 0 | 0 | 0.999 | 0 | 0 | 0 | A08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A08 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
9 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | 5% THDi Passive Filter | 09 |  | A09 |  | 6 Pulse w/ No Impedance | 5% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A09 | 0 | 0 | 0.993 | 0 | 0 | 0 | A09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A09 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
10 | [5 empty] | 0 | 1 | 0 | 32.8
11 | [5 empty] | 0 | 1 | 0 | 32.8
12 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Revision | 220705P |  |  |  | B00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
13 | [5 empty] | 0 | 1 | 0 | 32.8 | [6 empty] | B01 |  | 6 Pulse w/ 3% Impedance | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B01 | 0 | 0 | 0.985 | 0 | 0 | 0 | B01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 3.0026
14 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Source Selection | UTILITY | System Values |  |  | B02 |  | 6 Pulse w/ 3% Impedance | 1.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B02 | 0 | 0 | 0.983 | 0 | 0 | 0 | B02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B02 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 4.5026
15 | [5 empty] | 0 | 1 | 0 | 32.8 |  | UTILITY |  | freq [Hz] | 60 |  | B03 |  | 6 Pulse w/ 3% Impedance | 2.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B03 | 0 | 0 | 0.979 | 0 | 0 | 0 | B03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B03 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 5.5026
16 | [5 empty] | 0 | 1 | 0 | 32.8 |  | GENERATOR |  | Vbus [V] | 480 |  | B04 |  | 6 Pulse w/ 3% Impedance | 3% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B04 | 0 | 0 | 0.978 | 0 | 0 | 0 | B04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B04 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 6.0026
17 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Isc [kA] | 38.49 |  | B05 |  | 6 Pulse w/ 3% Impedance | 5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B05 | 0 | 0 | 0.97 | 0 | 0 | 0 | B05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B05 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 8.0026
18 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Source [uH] | 19.0986 |  | B06 |  | 6 Pulse w/ 3% Impedance | 7% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B06 | 0 | 0 | 0.963 | 0 | 0 | 0 | B06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B06 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 10.0026
19 | [5 empty] | 0 | 1 | 0 | 32.8 |  | PCC Selection | XFMR Pri |  |  |  | B07 |  | 6 Pulse w/ 3% Impedance | 10% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B07 | 0 | 0 | 0.951 | 0 | 0 | 0 | B07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B07 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 13.0026
20 | [5 empty] | 0 | 1 | 0 | 32.8 |  | XFMR Pri |  |  |  |  | B08 |  | 6 Pulse w/ 3% Impedance | 7% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B08 | 0 | 0 | 0.999 | 0 | 0 | 0 | B08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B08 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 3.0026
21 | [5 empty] | 0 | 1 | 0 | 32.8 |  | XFMR Sec |  |  |  |  | B09 |  | 6 Pulse w/ 3% Impedance | 5% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B09 | 0 | 0 | 0.993 | 0 | 0 | 0 | B09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B09 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 3.0026
22 | [5 empty] | 0 | 1 | 0 | 32.8 |  | GEN Bus |  | System Constants
23 | [5 empty] | 0 | 1 | 0 | 32.8
24 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | motor efficiency [pu] | 0.95 |  | C00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
25 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Units Selection | US | drive efficiency [pu] | 0.97 |  | C01 |  | 6 Pulse w/ 5% Impedance | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C01 | 0 | 0 | 0.992 | 0 | 0 | 0 | C01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 5.0026
26 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | input cable [ft] | 32.8 |  | C02 |  | 6 Pulse w/ 5% Impedance | 1.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C02 | 0 | 0 | 0.986 | 0 | 0 | 0 | C02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C02 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 6.5026
27 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | cable inductance [uH/m] | 0.435 |  | C03 |  | 6 Pulse w/ 5% Impedance | 2.5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C03 | 0 | 0 | 0.982 | 0 | 0 | 0 | C03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C03 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 7.5026
28 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Linear Load Selection | Max Percent of Source | xfmr with delta winding | Y |  | C04 |  | 6 Pulse w/ 5% Impedance | 3% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C04 | 0 | 0 | 0.98 | 0 | 0 | 0 | C04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C04 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 8.0026
29 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Max Percent of Source |  |  |  |  | C05 |  | 6 Pulse w/ 5% Impedance | 5% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C05 | 0 | 0 | 0.972 | 0 | 0 | 0 | C05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C05 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 10.0026
30 | [5 empty] | 0 | 1 | 0 | 32.8 |  | Itemized |  | 7% THDi Filter, no load amps | -35 |  | C06 |  | 6 Pulse w/ 5% Impedance | 7% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C06 | 0 | 0 | 0.964 | 0 | 0 | 0 | C06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C06 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 12.0026
31 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | 5% THDi Filter, no load amps | -40 |  | C07 |  | 6 Pulse w/ 5% Impedance | 10% AC Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C07 | 0 | 0 | 0.952 | 0 | 0 | 0 | C07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C07 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 15.0026
32 | [5 empty] | 0 | 1 | 0 | 32.8 | [6 empty] | C08 |  | 6 Pulse w/ 5% Impedance | 7% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C08 | 0 | 0 | 0.999 | 0 | 0 | 0 | C08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C08 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 5.0026
33 | [5 empty] | 0 | 1 | 0 | 32.8 | [6 empty] | C09 |  | 6 Pulse w/ 5% Impedance | 5% THDi Passive Filter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C09 | 0 | 0 | 0.993 | 0 | 0 | 0 | C09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C09 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 5.0026
34 | [5 empty] | 0 | 1 | 0 | 32.8
35 | [5 empty] | 0 | 1 | 0 | 32.8
36 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Input Info |  |  | D00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
37 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | System Freq [Hz] | 60 |  | D01 |  | 12 Pulse Drive | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D01 | 0 | 0 | 0.981 | 0 | 0 | 0 | D01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
38 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Utility [kV] | 13800 |  | D02 | X | 12 Pulse Drive | 1.5% AC Reactor
39 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Utility [MVAsc] | 400 |  | D03 | X | 12 Pulse Drive | 2.5% AC Reactor
40 | [5 empty] | 0 | 1 | 0 | 32.8 | [6 empty] | D04 | X | 12 Pulse Drive | 3% AC Reactor
41 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Transformer |  |  | D05 | X | 12 Pulse Drive | 5% AC Reactor
42 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Rated kVA [kVA] | 2000 |  | D06 | X | 12 Pulse Drive | 7% AC Reactor
43 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Secondary Voltge [V] | 480 |  | D07 | X | 12 Pulse Drive | 10% AC Reactor
44 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Impedance [%Z] | 5.75 |  | D08 | X | 12 Pulse Drive | 7% THDi Passive Filter
45 | [5 empty] | 0 | 1 | 0 | 32.8 | [6 empty] | D09 | X | 12 Pulse Drive | 5% THDi Passive Filter
46 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Linear Loads |  | PF
47 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Total HP motor loads [hp] | 0 | 0.85
48 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Total kW resistive loads [kW] | 0 | 1 | E00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
49 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Total kVA loads [kVA] | 0 | 0.9 | E01 |  | 18 Pulse Drive | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E01 | 0 | 0 | 0.985 | 0 | 0 | 0 | E01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
50 | [5 empty] | 0 | 1 | 0 | 32.8 |  |  |  | Total ampere loads [A] | 0 | 0.9 | E02 | X | 18 Pulse Drive | 1.5% AC Reactor
[13 empty] | MAX % kVA loading of xfmr [%] | 70 | 0.9 | E03 | X | 18 Pulse Drive | 2.5% AC Reactor
[13 empty] | MAX % kW loading of gen [%] | 100 | 0.9 | E04 | X | 18 Pulse Drive | 3% AC Reactor
[16 empty] | E05 | X | 18 Pulse Drive | 5% AC Reactor
[13 empty] | Generator |  |  | E06 | X | 18 Pulse Drive | 7% AC Reactor
[13 empty] | Rated Power [kW] | 2000 |  | E07 | X | 18 Pulse Drive | 10% AC Reactor
[13 empty] | Power Factor [pu] | 0.8 |  | E08 | X | 18 Pulse Drive | 7% THDi Passive Filter
[13 empty] | Apparent Power [kVA] | 2500 |  | E09 | X | 18 Pulse Drive | 5% THDi Passive Filter
[13 empty] | Output Voltage [V] | 480
[13 empty] | Xd" | 0.2
[16 empty] | F00 |  | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
[16 empty] | F01 |  | ULH (AFE) Drive | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F01 | 0 | 0 | 0.995 | 0 | 0 | 0 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179 | 0.1
[5 empty] | Messages: | [5 empty] | Design Checks |  |  |  |  | F02 | X | ULH (AFE) Drive | 1.5% AC Reactor
[5 empty] | No power limits exceeded |  |  |  |  | 1 | No power limits exceeded |  |  |  |  | F03 | X | ULH (AFE) Drive | 2.5% AC Reactor
[5 empty] | Total kVA load exceeds the MAX % kVA loading! |  |  |  |  | 2 | [5 empty] | F04 | X | ULH (AFE) Drive | 3% AC Reactor
[5 empty] | Total kVA load exceeds the Transformer kVA rating! |  |  |  |  | 3 | [5 empty] | F05 | X | ULH (AFE) Drive | 5% AC Reactor
[5 empty] | Total kW load exceeds the MAX % kW loading! |  |  |  |  | 4 | [5 empty] | F06 | X | ULH (AFE) Drive | 7% AC Reactor
[5 empty] | Total kW load exceeds the Generator kW rating! |  |  |  |  | 5 | [5 empty] | F07 | X | ULH (AFE) Drive | 10% AC Reactor
[5 empty] | Total kVA load exceeds the Generator kVA rating! |  |  |  |  | 6 | [5 empty] | F08 | X | ULH (AFE) Drive | 7% THDi Passive Filter
[16 empty] | F09 | X | ULH (AFE) Drive | 5% THDi Passive Filter
[18 empty] | Drive | Filter | Count | total rated HP | total actual HP | avg pu load | total ft | avg ft | avg m |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] |  | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%] |  | X source [uH] | X cable [uH] | x total [uH] | Isc | Isc / Ifund | %Z
[16 empty] | G01 |  | Custom System | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G01 | 0 | 0 | 0.97 | 0 | 0 | 0 | G01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G01 | 19.0986 | 0 | 19.0986 | 38490.0179 | 38490.0179
[16 empty] | G02 | X | Custom System | 1.5% AC Reactor
[16 empty] | G03 | X | Custom System | 2.5% AC Reactor
[16 empty] | G04 | X | Custom System | 3% AC Reactor
[16 empty] | G05 | X | Custom System | 5% AC Reactor
[16 empty] | G06 | X | Custom System | 7% AC Reactor
[16 empty] | G07 | X | Custom System | 10% AC Reactor
[16 empty] | G08 | X | Custom System | 7% THDi Passive Filter
[16 empty] | G09 | X | Custom System | 5% THDi Passive Filter

## Sum (hidden)
| Summary Calculations | [30 empty] | PCC2 | PCC2 | PCC2 | PCC2 |  | PCC2 | PCC2 | PCC2 | PCC2 | PCC2 |  | PCC1 | PCC1 | PCC1 | PCC1 | PCC1 | K-Factor at PCC2 |  |  |  |  | Report Info |  |  | Plotting Info
Harm No | A01 | A02 | A03 | A04 | A05 | A06 | A07 | A08 | A09 | B01 | B02 | B03 | B04 | B05 | B06 | B07 | B08 | B09 | C01 | C02 | C03 | C04 | C05 | C06 | C07 | C08 | C09 | D01 | E01 | F01 | Custom | Drive Sum | Lin Load | subtotal | AHF |  | Itotal | % of I1 fund | source X | Vsource | % of V1 |  | Itotal | % of I1 | Utility | Vutility | % of V1 | h | Ih | N=Ih/rss | N*h |  |  | XFMR Pri | XFMR Sec |  | XFMR Pri |  | XFMR Sec
[35 empty] | 0 |  |  |  | X [uO] |  |  |  | 28.75 |  | X [uO] | [7 empty] | h | Ih | Vh
1 real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1515.5445 | 1515.5445 |  |  | 1515.5445 | 90 |  |  |  |  | 52.7146 | 90
1 react | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.0117 | 734.0117 |  |  | 734.0117 | 43.589 |  |  |  |  | 25.5308 | 43.589
1 fund | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1683.9383 | 1683.9383 | 0 |  | 1683.9383 | 100 | 7200 | 277.1281 | 100 |  | 58.5718 | 100 | 476100 | 7967.4337 | 100 | 1 | 1683.9383 | 1 | 1 |  | 1 | 58.5718 | 277.1281 |  | Ih % |  | Vh %
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 14400 | 0 | 0 |  | 0 | 0 | 952200 | 0 | 0 | 2 | 0 | 0 | 0 |  | 2 | 0 | 0 | 2 | 0 | 2 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 21600 | 0 | 0 |  | 0 | 0 | 1428300 | 0 | 0 | 3 | 0 | 0 | 0 |  | 3 | 0 | 0 | 3 | 0 | 3 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 28800 | 0 | 0 |  | 0 | 0 | 1904400 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4 | 0 | 0 | 4 | 0 | 4 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 36000 | 0 | 0 |  | 0 | 0 | 2380500 | 0 | 0 | 5 | 0 | 0 | 0 |  | 5 | 0 | 0 | 5 | 0 | 5 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 43200 | 0 | 0 |  | 0 | 0 | 2856600 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6 | 0 | 0 | 6 | 0 | 6 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 50400 | 0 | 0 |  | 0 | 0 | 3332700 | 0 | 0 | 7 | 0 | 0 | 0 |  | 7 | 0 | 0 | 7 | 0 | 7 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 57600 | 0 | 0 |  | 0 | 0 | 3808800 | 0 | 0 | 8 | 0 | 0 | 0 |  | 8 | 0 | 0 | 8 | 0 | 8 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 64800 | 0 | 0 |  | 0 | 0 | 4284900 | 0 | 0 | 9 | 0 | 0 | 0 |  | 9 | 0 | 0 | 9 | 0 | 9 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 72000 | 0 | 0 |  | 0 | 0 | 4761000 | 0 | 0 | 10 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 10 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 79200 | 0 | 0 |  | 0 | 0 | 5237100 | 0 | 0 | 11 | 0 | 0 | 0 |  | 11 | 0 | 0 | 11 | 0 | 11 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 86400 | 0 | 0 |  | 0 | 0 | 5713200 | 0 | 0 | 12 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 12 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 93600 | 0 | 0 |  | 0 | 0 | 6189300 | 0 | 0 | 13 | 0 | 0 | 0 |  | 13 | 0 | 0 | 13 | 0 | 13 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 100800 | 0 | 0 |  | 0 | 0 | 6665400 | 0 | 0 | 14 | 0 | 0 | 0 |  | 14 | 0 | 0 | 14 | 0 | 14 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 108000 | 0 | 0 |  | 0 | 0 | 7141500 | 0 | 0 | 15 | 0 | 0 | 0 |  | 15 | 0 | 0 | 15 | 0 | 15 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 115200 | 0 | 0 |  | 0 | 0 | 7617600 | 0 | 0 | 16 | 0 | 0 | 0 |  | 16 | 0 | 0 | 16 | 0 | 16 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 122400 | 0 | 0 |  | 0 | 0 | 8093700 | 0 | 0 | 17 | 0 | 0 | 0 |  | 17 | 0 | 0 | 17 | 0 | 17 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 129600 | 0 | 0 |  | 0 | 0 | 8569800 | 0 | 0 | 18 | 0 | 0 | 0 |  | 18 | 0 | 0 | 18 | 0 | 18 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 136800 | 0 | 0 |  | 0 | 0 | 9045900 | 0 | 0 | 19 | 0 | 0 | 0 |  | 19 | 0 | 0 | 19 | 0 | 19 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 144000 | 0 | 0 |  | 0 | 0 | 9522000 | 0 | 0 | 20 | 0 | 0 | 0 |  | 20 | 0 | 0 | 20 | 0 | 20 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 151200 | 0 | 0 |  | 0 | 0 | 9998100 | 0 | 0 | 21 | 0 | 0 | 0 |  | 21 | 0 | 0 | 21 | 0 | 21 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 158400 | 0 | 0 |  | 0 | 0 | 10474200 | 0 | 0 | 22 | 0 | 0 | 0 |  | 22 | 0 | 0 | 22 | 0 | 22 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 165600 | 0 | 0 |  | 0 | 0 | 10950300 | 0 | 0 | 23 | 0 | 0 | 0 |  | 23 | 0 | 0 | 23 | 0 | 23 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 172800 | 0 | 0 |  | 0 | 0 | 11426400 | 0 | 0 | 24 | 0 | 0 | 0 |  | 24 | 0 | 0 | 24 | 0 | 24 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 180000 | 0 | 0 |  | 0 | 0 | 11902500 | 0 | 0 | 25 | 0 | 0 | 0 |  | 25 | 0 | 0 | 25 | 0 | 25 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 187200 | 0 | 0 |  | 0 | 0 | 12378600 | 0 | 0 | 26 | 0 | 0 | 0 |  | 26 | 0 | 0 | 26 | 0 | 26 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 194400 | 0 | 0 |  | 0 | 0 | 12854700 | 0 | 0 | 27 | 0 | 0 | 0 |  | 27 | 0 | 0 | 27 | 0 | 27 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 201600 | 0 | 0 |  | 0 | 0 | 13330800 | 0 | 0 | 28 | 0 | 0 | 0 |  | 28 | 0 | 0 | 28 | 0 | 28 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 208800 | 0 | 0 |  | 0 | 0 | 13806900 | 0 | 0 | 29 | 0 | 0 | 0 |  | 29 | 0 | 0 | 29 | 0 | 29 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 216000 | 0 | 0 |  | 0 | 0 | 14283000 | 0 | 0 | 30 | 0 | 0 | 0 |  | 30 | 0 | 0 | 30 | 0 | 30 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 223200 | 0 | 0 |  | 0 | 0 | 14759100 | 0 | 0 | 31 | 0 | 0 | 0 |  | 31 | 0 | 0 | 31 | 0 | 31 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 230400 | 0 | 0 |  | 0 | 0 | 15235200 | 0 | 0 | 32 | 0 | 0 | 0 |  | 32 | 0 | 0 | 32 | 0 | 32 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 237600 | 0 | 0 |  | 0 | 0 | 15711300 | 0 | 0 | 33 | 0 | 0 | 0 |  | 33 | 0 | 0 | 33 | 0 | 33 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 244800 | 0 | 0 |  | 0 | 0 | 16187400 | 0 | 0 | 34 | 0 | 0 | 0 |  | 34 | 0 | 0 | 34 | 0 | 34 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 252000 | 0 | 0 |  | 0 | 0 | 16663500 | 0 | 0 | 35 | 0 | 0 | 0 |  | 35 | 0 | 0 | 35 | 0 | 35 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 259200 | 0 | 0 |  | 0 | 0 | 17139600 | 0 | 0 | 36 | 0 | 0 | 0 |  | 36 | 0 | 0 | 36 | 0 | 36 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 266400 | 0 | 0 |  | 0 | 0 | 17615700 | 0 | 0 | 37 | 0 | 0 | 0 |  | 37 | 0 | 0 | 37 | 0 | 37 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 273600 | 0 | 0 |  | 0 | 0 | 18091800 | 0 | 0 | 38 | 0 | 0 | 0 |  | 38 | 0 | 0 | 38 | 0 | 38 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 280800 | 0 | 0 |  | 0 | 0 | 18567900 | 0 | 0 | 39 | 0 | 0 | 0 |  | 39 | 0 | 0 | 39 | 0 | 39 | 0
40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 288000 | 0 | 0 |  | 0 | 0 | 19044000 | 0 | 0 | 40 | 0 | 0 | 0 |  | 40 | 0 | 0 | 40 | 0 | 40 | 0
41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 295200 | 0 | 0 |  | 0 | 0 | 19520100 | 0 | 0 | 41 | 0 | 0 | 0 |  | 41 | 0 | 0 | 41 | 0 | 41 | 0
42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 302400 | 0 | 0 |  | 0 | 0 | 19996200 | 0 | 0 | 42 | 0 | 0 | 0 |  | 42 | 0 | 0 | 42 | 0 | 42 | 0
43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 309600 | 0 | 0 |  | 0 | 0 | 20472300 | 0 | 0 | 43 | 0 | 0 | 0 |  | 43 | 0 | 0 | 43 | 0 | 43 | 0
44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 316800 | 0 | 0 |  | 0 | 0 | 20948400 | 0 | 0 | 44 | 0 | 0 | 0 |  | 44 | 0 | 0 | 44 | 0 | 44 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 324000 | 0 | 0 |  | 0 | 0 | 21424500 | 0 | 0 | 45 | 0 | 0 | 0 |  | 45 | 0 | 0 | 45 | 0 | 45 | 0
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 331200 | 0 | 0 |  | 0 | 0 | 21900600 | 0 | 0 | 46 | 0 | 0 | 0 |  | 46 | 0 | 0 | 46 | 0 | 46 | 0
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 338400 | 0 | 0 |  | 0 | 0 | 22376700 | 0 | 0 | 47 | 0 | 0 | 0 |  | 47 | 0 | 0 | 47 | 0 | 47 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 345600 | 0 | 0 |  | 0 | 0 | 22852800 | 0 | 0 | 48 | 0 | 0 | 0 |  | 48 | 0 | 0 | 48 | 0 | 48 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 352800 | 0 | 0 |  | 0 | 0 | 23328900 | 0 | 0 | 49 | 0 | 0 | 0 |  | 49 | 0 | 0 | 49 | 0 | 49 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 360000 | 0 | 0 |  | 0 | 0 | 23805000 | 0 | 0 | 50 | 0 | 0 | 0 |  | 50 | 0 | 0 | 50 | 0 | 50 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 367200 | 0 | 0 |  | 0 | 0 | 24281100 | 0 | 0 | 51 | 0 | 0 | 0 |  | 51 | 0 | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 374400 | 0 | 0 |  | 0 | 0 | 24757200 | 0 | 0 | 52 | 0 | 0 | 0 |  | 52 | 0 | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 381600 | 0 | 0 |  | 0 | 0 | 25233300 | 0 | 0 | 53 | 0 | 0 | 0 |  | 53 | 0 | 0 | TDD | 0 | vTHD | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 388800 | 0 | 0 |  | 0 | 0 | 25709400 | 0 | 0 | 54 | 0 | 0 | 0 |  | 54 | 0 | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 396000 | 0 | 0 |  | 0 | 0 | 26185500 | 0 | 0 | 55 | 0 | 0 | 0 |  | 55 | 0 | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 403200 | 0 | 0 |  | 0 | 0 | 26661600 | 0 | 0 | 56 | 0 | 0 | 0 |  | 56 | 0 | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 410400 | 0 | 0 |  | 0 | 0 | 27137700 | 0 | 0 | 57 | 0 | 0 | 0 |  | 57 | 0 | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 417600 | 0 | 0 |  | 0 | 0 | 27613800 | 0 | 0 | 58 | 0 | 0 | 0 |  | 58 | 0 | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 424800 | 0 | 0 |  | 0 | 0 | 28089900 | 0 | 0 | 59 | 0 | 0 | 0 |  | 59 | 0 | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 432000 | 0 | 0 |  | 0 | 0 | 28566000 | 0 | 0 | 60 | 0 | 0 | 0 |  | 60 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 439200 | 0 | 0 |  | 0 | 0 | 29042100 | 0 | 0 | 61 | 0 | 0 | 0 |  | 61 | 0 | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 446400 | 0 | 0 |  | 0 | 0 | 29518200 | 0 | 0 | 62 | 0 | 0 | 0 |  | 62 | 0 | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 453600 | 0 | 0 |  | 0 | 0 | 29994300 | 0 | 0 | 63 | 0 | 0 | 0 |  | 63 | 0 | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 460800 | 0 | 0 |  | 0 | 0 | 30470400 | 0 | 0 | 64 | 0 | 0 | 0 |  | 64 | 0 | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 468000 | 0 | 0 |  | 0 | 0 | 30946500 | 0 | 0 | 65 | 0 | 0 | 0 |  | 65 | 0 | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 475200 | 0 | 0 |  | 0 | 0 | 31422600 | 0 | 0 | 66 | 0 | 0 | 0 |  | 66 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 482400 | 0 | 0 |  | 0 | 0 | 31898700 | 0 | 0 | 67 | 0 | 0 | 0 |  | 67 | 0 | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 489600 | 0 | 0 |  | 0 | 0 | 32374800 | 0 | 0 | 68 | 0 | 0 | 0 |  | 68 | 0 | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 496800 | 0 | 0 |  | 0 | 0 | 32850900 | 0 | 0 | 69 | 0 | 0 | 0 |  | 69 | 0 | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 504000 | 0 | 0 |  | 0 | 0 | 33327000 | 0 | 0 | 70 | 0 | 0 | 0 |  | 70 | 0 | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 511200 | 0 | 0 |  | 0 | 0 | 33803100 | 0 | 0 | 71 | 0 | 0 | 0 |  | 71 | 0 | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 518400 | 0 | 0 |  | 0 | 0 | 34279200 | 0 | 0 | 72 | 0 | 0 | 0 |  | 72 | 0 | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 525600 | 0 | 0 |  | 0 | 0 | 34755300 | 0 | 0 | 73 | 0 | 0 | 0 |  | 73 | 0 | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 532800 | 0 | 0 |  | 0 | 0 | 35231400 | 0 | 0 | 74 | 0 | 0 | 0 |  | 74 | 0 | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 540000 | 0 | 0 |  | 0 | 0 | 35707500 | 0 | 0 | 75 | 0 | 0 | 0 |  | 75 | 0 | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 547200 | 0 | 0 |  | 0 | 0 | 36183600 | 0 | 0 | 76 | 0 | 0 | 0 |  | 76 | 0 | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 554400 | 0 | 0 |  | 0 | 0 | 36659700 | 0 | 0 | 77 | 0 | 0 | 0 |  | 77 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 561600 | 0 | 0 |  | 0 | 0 | 37135800 | 0 | 0 | 78 | 0 | 0 | 0 |  | 78 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 568800 | 0 | 0 |  | 0 | 0 | 37611900 | 0 | 0 | 79 | 0 | 0 | 0 |  | 79 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 576000 | 0 | 0 |  | 0 | 0 | 38088000 | 0 | 0 | 80 | 0 | 0 | 0 |  | 80 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 583200 | 0 | 0 |  | 0 | 0 | 38564100 | 0 | 0 | 81 | 0 | 0 | 0 |  | 81 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 590400 | 0 | 0 |  | 0 | 0 | 39040200 | 0 | 0 | 82 | 0 | 0 | 0 |  | 82 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 597600 | 0 | 0 |  | 0 | 0 | 39516300 | 0 | 0 | 83 | 0 | 0 | 0 |  | 83 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 604800 | 0 | 0 |  | 0 | 0 | 39992400 | 0 | 0 | 84 | 0 | 0 | 0 |  | 84 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 612000 | 0 | 0 |  | 0 | 0 | 40468500 | 0 | 0 | 85 | 0 | 0 | 0 |  | 85 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 619200 | 0 | 0 |  | 0 | 0 | 40944600 | 0 | 0 | 86 | 0 | 0 | 0 |  | 86 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 626400 | 0 | 0 |  | 0 | 0 | 41420700 | 0 | 0 | 87 | 0 | 0 | 0 |  | 87 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 633600 | 0 | 0 |  | 0 | 0 | 41896800 | 0 | 0 | 88 | 0 | 0 | 0 |  | 88 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 640800 | 0 | 0 |  | 0 | 0 | 42372900 | 0 | 0 | 89 | 0 | 0 | 0 |  | 89 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 648000 | 0 | 0 |  | 0 | 0 | 42849000 | 0 | 0 | 90 | 0 | 0 | 0 |  | 90 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 655200 | 0 | 0 |  | 0 | 0 | 43325100 | 0 | 0 | 91 | 0 | 0 | 0 |  | 91 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 662400 | 0 | 0 |  | 0 | 0 | 43801200 | 0 | 0 | 92 | 0 | 0 | 0 |  | 92 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 669600 | 0 | 0 |  | 0 | 0 | 44277300 | 0 | 0 | 93 | 0 | 0 | 0 |  | 93 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 676800 | 0 | 0 |  | 0 | 0 | 44753400 | 0 | 0 | 94 | 0 | 0 | 0 |  | 94 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 684000 | 0 | 0 |  | 0 | 0 | 45229500 | 0 | 0 | 95 | 0 | 0 | 0 |  | 95 | 0 | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 691200 | 0 | 0 |  | 0 | 0 | 45705600 | 0 | 0 | 96 | 0 | 0 | 0 |  | 96 | 0 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 698400 | 0 | 0 |  | 0 | 0 | 46181700 | 0 | 0 | 97 | 0 | 0 | 0 |  | 97 | 0 | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 705600 | 0 | 0 |  | 0 | 0 | 46657800 | 0 | 0 | 98 | 0 | 0 | 0 |  | 98 | 0 | 0
99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 712800 | 0 | 0 |  | 0 | 0 | 47133900 | 0 | 0 | 99 | 0 | 0 | 0 |  | 99 | 0 | 0
100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 720000 | 0 | 0 |  | 0 | 0 | 47610000 | 0 | 0 | 100 | 0 | 0 | 0 |  | 100 | 0 | 0
Iharm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Iharm | 0 | 0 | Vharm | 0 | 0 | Iharm | 0 | 0 | Vharm | 0 | 0 | RSS = | 1683.9383 | SS = | 1 | =K-Factor
Ifund | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1683.9383 | 1683.9383 | 0 | Ifund | 1683.9383 | 100 | Vfund | 277.1281 | 100 | Ifund | 58.5718 | 100 | Vfund | 7967.4337 | 100
Itotal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1683.9383 | 1683.9383 | 0 | Itotal | 1683.9383 | 100 | Vtotal | 277.1281 | 100 | Itotal | 58.5718 | 100 | Vtotal | 7967.4337 | 100
Ithd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ithd | 0 | 0 | Vthd | 0 | 0 | Ithd | 0 | 0 | Vthd | 0 | 0
| A01 | A02 | A03 | A04 | A05 | A06 | A07 | A08 | A09 | B01 | B02 | B03 | B04 | B05 | B06 | B07 | B08 | B09 | C01 | C02 | C03 | C04 | C05 | C06 | C07 | C08 | C09 | D01 | E01 | F01 | Custom | Drive Sum | Lin Load | subtotal | AHF |  | Itotal
[43 empty] | NOTE: | if the transformer has a delta winding, triplin harmonic currents are not present in the primary
[32 empty] | NOTE: | sum(h1:h7) | [9 empty] | 0.05 | Multiplier for the delta winding
sqrt(sumsq(h8:h100))
Note on AK3: Rick L. Hoadley: multiplying factor

## IEEE (hidden)
IEEE 519-2014
|  | XFMR Pri | XFMR Sec | GEN bus | Table 2 |  |  | IEEE Limits
[5 empty] | Isc/Iload | Itdd | h | 5% | 8% | 12% | 15% | 20%
[5 empty] | 0 | 5 | 1 | 100 | 100 | 100 | 100 | 100
| % Ithd | 0 | 0 | 0 | 20 | 8 | 2 | 1 | 1.75 | 2.5 | 3 | 3.75
| Isc/Iload | 285.7143 | 22.8571 | 8.9286 | 50 | 12 | 3 | 4 | 7 | 10 | 12 | 15
| Ithd Limit | 15 | 8 | 5 | 100 | 15 | 4 | 1 | 1.75 | 2.5 | 3 | 3.75
| IEEE | YES | YES | YES | 1000 | 20 | 5 | 4 | 7 | 10 | 12 | 15
[7 empty] | 6 | 1 | 1.75 | 2.5 | 3 | 3.75
[7 empty] | 7 | 4 | 7 | 10 | 12 | 15
| % Vthd | 0 |  |  |  |  | 8 | 1 | 1.75 | 2.5 | 3 | 3.75
| kV | 0.48 |  |  | Table 1 |  | 9 | 4 | 7 | 10 | 12 | 15
| Vthd Limit | 8 |  |  | kV bus | Vthd | 10 | 1 | 1.75 | 2.5 | 3 | 3.75
| IEEE | YES |  |  | 0 | 8 | 11 | 2 | 3.5 | 4.5 | 5.5 | 7
[5 empty] | 1 | 5 | 12 | 0.5 | 0.875 | 1.125 | 1.375 | 1.75
[5 empty] | 69 | 2.5 | 13 | 2 | 3.5 | 4.5 | 5.5 | 7
[5 empty] | 161 | 1.5 | 14 | 0.5 | 0.875 | 1.125 | 1.375 | 1.75
[7 empty] | 15 | 2 | 3.5 | 4.5 | 5.5 | 7
[7 empty] | 16 | 0.5 | 0.875 | 1.125 | 1.375 | 1.75
[7 empty] | 17 | 1.5 | 2.5 | 4 | 5 | 6
[7 empty] | 18 | 0.375 | 0.625 | 1 | 1.25 | 1.5
[7 empty] | 19 | 1.5 | 2.5 | 4 | 5 | 6
[7 empty] | 20 | 0.375 | 0.625 | 1 | 1.25 | 1.5
[7 empty] | 21 | 1.5 | 2.5 | 4 | 5 | 6
[7 empty] | 22 | 0.375 | 0.625 | 1 | 1.25 | 1.5
[7 empty] | 23 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 24 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 25 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 26 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 27 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 28 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 29 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 30 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 31 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 32 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 33 | 0.6 | 1 | 1.5 | 2 | 2.5
[7 empty] | 34 | 0.15 | 0.25 | 0.375 | 0.5 | 0.625
[7 empty] | 35 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 36 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 37 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 38 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 39 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 40 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 41 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 42 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 43 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 44 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 45 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 46 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 47 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 48 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | 49 | 0.3 | 0.5 | 0.7 | 1 | 1.4
[7 empty] | 50 | 0.075 | 0.125 | 0.175 | 0.25 | 0.35
[7 empty] | TDD | 5 | 8 | 12 | 15 | 20

## Power (hidden)
Power Details
[6 empty] | drives, linear loads |  |  |  | drives, linear loads, % xfmr |  | future feature |  | drives, linear loads, % xfmr, AHF | [7 empty] | Source: | UTILITY
Drives |  |  | Linear Loads |  |  | Sub-Totals |  | % xfmr |  | Sub-Totals |  | AHF |  | TOTALS |  | Utility |  | Transformer |  | Generator |  | Drive Source
0 | total rated hp |  | 0 | total kW motor loads | [7 empty] | 0 | A |  |  | 60 | Hz | 2000 | kVA | 2500 | kVA | 2000 | kVA
0 | total actual hp |  | 0 | total kW resistive loads | [7 empty] | 0 | 90% |  |  | 13800 | V | 480 | V | 480 | V | 480 | V
0 | avg pu load |  | 0 | total kVA loads | [7 empty] | 0 | Iharm |  |  | 400 | MVAsc | 28.75 | xfmr E1/E2 | 2000 | kW
0 | total ft |  | 0 | total A loads | [7 empty] | 0 | ratio |  |  |  |  | 5.75 | %Z | 0.2 | Xd" [pu] | 5.75 | %Z
0 | no of units |  | 0 | Ireal motors | [7 empty] | #REF! | qty |  |  |  |  | 2405.6261 | Irated | 3007.0327 | Irated | 2405.6261 | Irated
#DIV/0! | avg ft |  | 0 | Ireact motors | [7 empty] | 0 | factor |  |  | 16.7348 | Isc [kA] | 41.837 | Isc [kA] | 15.0352 | Isc [kA] | 38.49 | Isc [kA]
#DIV/0! | avg m |  | 0 | Ireal resistive | [11 empty] | 400 | MVAsc | 34.7826 | MVAsc | 12.5 | MVAsc | 32 | MVAsc
|  |  | 0 | Ireal kVA loads
|  |  | 0 | Ireact kVA loads | [13 empty] | 6624 | X xfmr [uO] | 0.8 | PFrated | PCC for Itdd | XFMR Pri
|  |  | 0 | Ireal A loads | [13 empty] | 17.5707 | X xfmr [uH] | 2405.6261 | Ireal rated | PCC for Vthd | XFMR Sec
|  |  | 0 | Ireact A loads | [17 empty] | Lin Load Sel | Max Percent of Source
0 | Pin rated, [kW]
0 | Pin actual [kW] |  | 0 | kW |  | 0 | kW | 1260 | kW | 1260 | kW | 0 | kW | 1260 | kW
0 | Qin, [kVAR] |  | 0 | kVAR |  | 0 | kVAR | 610.2459 | kVAR | 610.2459 | kVAR | 0 | kVAR | 610.2459 | kVAR | Primary side of xfmr |  | Secondary side of xfmr |  | Generator bus |  | Source for Drives
0 | Din, [kVAD] |  | 0 | kVAD |  | 0 | kVAD | 0 | kVAD | 0 | kVAD | 0 | kVAD | 0 | kVAD | 476100 | X utility [uO] | 7200 | X source [uO] | 18432 | X gen [uO] | 7200 | Source [uO]
0 | Sin, [kVA] |  | 0 | kVA |  | 0 | kVA | 1400 | kVA | 1400 | kVA | 0 | kVA | 1400 | kVA | 1262.8945 | X utility [uH] | 19.0986 | X source [uH] | 48.8924 | X gen [uH] | 19.0986 | Source [uH]
0 | PF disp |  | 0 | PF tot |  | 0 | PF tot | 0.9 | PF tot | 0.9 | PF tot | 0 | PF tot | 0.9 | PF tot
[16 empty] | 16.7348 | Isc [kA] | 38.49 | Isc [kA] | 15.0352 | Isc [kA] | 38.49 | Isc, [kA]
[16 empty] | 400 | MVAsc | 32 | MVAsc | 12.5 | MVAsc | 32 | MVAsc
0 | Ireal rated, [A] | [20 empty] | Report Information
0 | Ireal actual, [A] |  | 0 | Ireal |  | 0 | Ireal | 1515.5445 | Ireal | 1515.5445 | Ireal | 0 | Ireal | 1515.5445 | Ireal | 52.7146 | Ireal | 1515.5445 | Ireal | 1515.5445 | Ireal | 52.7146 | Ireal
0 | Ireact, [A] |  | 0 | Ireact |  | 0 | Ireact | 734.0117 | Ireact | 734.0117 | Ireact | 0 | Ireact | 734.0117 | Ireact | 25.5308 | Ireact | 734.0117 | Ireact | 734.0117 | Ireact | 25.5308 | Ireact
0 | Iharm, [A] |  | 0 | Iharm |  | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm | 0 | Iharm
0 | Ifund, [A] |  | 0 | Ifund |  | 0 | Ifund | 1683.9383 | Ifund | 1683.9383 | Ifund | 0 | Ifund | 1683.9383 | Ifund | 58.5718 | Ifund | 1683.9383 | Ifund | 1683.9383 | Ifund | 58.5718 | Ifund
0 | Itotal, [A] |  | 0 | Itotal |  | 0 | Itotal | 1683.9383 | Itotal | 1683.9383 | Itotal | 0 | Itotal | 1683.9383 | Itotal | 58.5718 | Itotal | 1683.9383 | Itotal | 1683.9383 | Itotal | 58.5718 | Itotal
0 | Ithd, [%] |  | 0 | Ithd |  | 0 | Ithd | 0 | Ithd | 0 | Ithd | 0 | Ithd | 0 | Ithd | 0 | TDD [%] | 0 | TDD [%] | 0 | TDD [%] | 0 | TDD [%]
0 | I_drive/I_load [%] |  | 0 | PF of lin load | [7 empty] | To meet TDD |  |  |  | 16.7348 | Isc [kA] | 38.49 | Isc [kA] | 15.0352 | Isc [kA] | 16.7348 | Isc [kA]
[8 empty] | Transformer Linear Load |  | linear loads, % xfmr |  | 15 | limit |  |  | 400 | MVAsc | 32 | MVAsc | 12.5 | MVAsc | 400 | MVAsc
[8 empty] | 0.9 | PF of lin load | 1515.5445 | Ireal | 252.5907 | Iharm |  |  | 285.7143 | Isc / Iload | 22.8571 | Isc / Iload | 8.9286 | Isc / Iload | 285.7143 | Isc / Iload
[8 empty] | 1683.9383 | Itotal goal | 734.0117 | Ireact |  |  |  |  | 15 | TDD Limit | 8 | TDD Limit | 5 | TDD Limit | 15 | TDD Limit [%]
[8 empty] | 1683.9383 | Ireal goal | 0 | Iharm | Present Iharm | [9 empty] | PASS | Meets TDD?
[8 empty] | 1683.9383 | Ireal delta | 1683.9383 | Ifund | 0 | Iharm
[8 empty] | 1515.5445 | Ireal adder | 1683.9383 | Itotal |  |  |  |  | 70 | goal on sec | 70 | % load goal | 100 | % load goal | 70 | % load goal
[8 empty] | 734.0117 | Ireact goal |  |  | Difference |  |  |  | 58.5718 | A goal | 1683.9383 | A goal | 2405.6261 | Ireal goal | 58.5718 | A goal
[8 empty] | 734.0117 | Ireact delta | 1400 | kVA | 0 | I_AHF |  |  |  |  | 70 | % actual | 63 | % actual | 70 | % actual
[8 empty] | 734.0117 | Ireact adder | 1260 | kW | 0 | extra |  |  |  |  | 1400 | kVA load goal | 2000 | kW load goal
[12 empty] | Min I for AHF | [5 empty] | 70 | % thermal |  |  | 1 | K-Factor
Generator Linear Load
|  | modified to set % kW load for gen |  |  | x |  |  | 0.9 | PF of lin load | [6 empty] | 13.8 | kV | 0.48 | kV | 0.48 | kV | 0.48 | kV
[8 empty] | 2405.6261 | Ireal target | [6 empty] | 0 | Vharm | 0 | Vharm | 0 | Vharm | 0 | Vharm
|  | need to show on input, load table: | [5 empty] | 2405.6261 | Ireal goal | [6 empty] | 7967.4337 | Vfund | 277.1281 | Vfund | 277.1281 | Vfund | 277.1281 | Vfund
|  | % kW load |  |  | x |  |  | 2405.6261 | Ireal delta | [6 empty] | 0 | vTHD | 0 | vTHD | 0 | vTHD | 0 | vTHD [%]
|  | % kVA load |  |  | x |  |  | 2405.6261 | Ireal adder | [12 empty] | 8 | vTHD Limit
|  | If either is exceeded |  |  | x |  |  | 1165.0979 | Ireact goal | [12 empty] | PASS | Meets vTHD?
|  | % current - drop this |  |  | x |  |  | 1165.0979 | Ireact delta
|  | and the conditional formatting |  |  | x |  |  | 1165.0979 | Ireact adder | [12 empty] | Total at: | XFMR Pri
[22 empty] | Amps | 58.5718
|  | OK as is for transformer |  |  | x | [16 empty] | kVA | 1400
[8 empty] | Source: | UTILITY | [12 empty] | kW | 1260
|  | gray out linear load section if NO? |  |  | do this |  |  | 1400 | load goal | [12 empty] | PF | 0.9
[8 empty] | 1515.5445 | Ireal adder | [12 empty] | kVA Goal | 1400
[8 empty] | 734.0117 | Ireact adder
Please note that the information shown here is typical and does not constitute any guarantee of performance or measurement. Several outside factors can influence the harmonics measured on a power system, including other equipment within the plant and other equipment in neighboring plants. This can include, but is not limited to, drives, varying loads and/or other factory equipment.
The calculated current and voltage harmonics shown in this report are for estimation purposes only.

## Thermal (hidden)
XFMR Thermal Load
K-Factor
|  | 2000 | kva | kva | 0 | 1000 | 1500
|  | 2405.6261 | rated current | Pec-r | 0.08 | 0.12 | 0.15
|  | 0.15 | Pec-r
|  | 1 | K-Factor | data from Grebe, 1994
|  | 1 | derating factor | data also from Paice, p114
|  | 2405.6261 | derated current
|  | 1683.9383 | Ifund
|  | 70 | % thermally loaded
| Irms |  |  | Irms values used for comparison only
|  | 2405.6261 | Irated
|  | 1683.9383 | Itotal
|  | 721.6878 | Irated-Iload
|  | 70 | % loaded

## Notes (hidden)
Notes |  | pw = 314159 |  |  |  |  | REV: | 220705P | p/w: | harmonics
Date | Notes
170503 | In Axx,Bxx,Cxx,Dxx,Exx,Fxx: changed PF to 0.910
PF disp for each combination is now set to 0.910 as found in Drives, column AG
In Drives: changed motor eff from 0.94 to 0.93, drive eff from 0.975 to 0.970
Now, 1000hp for a drive = 1093.052A, similar to version 5.1 that has 1094.3A for every type of drive/filter combination
V5.1 TDD now matches 170503 TDD
On F01, harmonics are % of fundamental, not Arms
Obtained additional harmonics from 5.1 for all tables by setting up various configurations and grabbing column AA on %TDD tab
For a 1.00% impedance system base, use the following:
|  | Source Selected | UTILITY
|  | Utility [V] | 13800
|  | Utility [MVAsc] | 400
Transformer ID Tag
|  | Rated kVA [kVA] | 2000
|  | Secondary Voltage [V] | 480
|  | Impedance [% Z] | 1.7
|  | % Loaded | 0
|  | PCC for TDD | XFMR Sec
|  | Drive | Filter | Rated HP | % Load
|  | 6 Pulse w/ 5% DC Choke | none | 1000 | 100%
Constants Used
|  | motor pf | 0.87
|  | motor eff | 0.93
|  | drive eff | 0.97
|  | cable uH/m | 0.435
|  | TCI HG7 Filter, I_NL | -35
|  | MTE Matrix Filter, I_NL | -40
|  | linear load pf | 1
|  | ft from PCC | 0
This is to help match the TDD with 5.1
170628 | added Generator % Loaded variable in Drives N42
Linked this to the Power W35
Fixed error in Power W17
Fixed error in Power E18
Noted PF tot in Power row 15
Rearranged Power rows 15-18
Moved Constants table from Drives to Instructions - a sheet that will not be hidden
Added note in Drives AY3
Added in Input R8 info from Input H67 (AHF current)
170706 | Added defaults for constants in Instructions
Added diagrams in Instructions
Per meeting today:
My notes for changes include:
| 1) | Worksheet areas on the input tab for:
|  | a. | kW to hp conversion - done
|  | b. | Amps and volts to hp conversion - done
|  | c. | Tons of chiller to hp conversion - done
|  | d. | Generator data to MVAsc conversion - in the report
| 2) | Add more empty cells for special qualifying notes - done
| 3) | Change % Loaded for generator to 100% - done
| 4) | Note that the Positive Sequence Isc is at the transformer primary - done
| 5) | Change "Filter" column to "Additional Filter" - done
| 6) | For the drive names, replace "DC Choke" with "Impedance" - done
| 7) | For the ULH drive, call it "ULH (AFE) Drive" - done
| 8) | For the filter names, replace "TCI HG7 Filter" with "7% THDi Filter" - done
| 9) | For the filter names, replace "MTE Matrix Filter" with "5% THDi Filter" - done
| 10) | Create the harmonic table for the TCI HGP filter and use that for the "5% THDi Filter" data - done
| 11) | Be able to use the harmonic tables at less than 100% load - done
| 12) | Create a "REPORT" tab with the following data
|  | a. | Page 1 has
|  |  | i. | Header information - done
|  |  | ii. | Source information - done
|  |  | iii. | Harmonic results and statement (pass/fail) - done
|  |  | iv. | Qualifying statements - done
|  |  | v. | AHF information if used - done
|  |  | vi. | Diagrams (if possible) - both shown for now
|  | b. | Page 2 has
|  |  | i. | VFD schedule with columns B through I - done
|  | c. | Page 3 has
|  |  | i. | Current and Voltage harmonic spectrum graphs - done
|  | d. | Have MARCOMM review for logo, colors, etc
| 13) | Set password to : harmonics - done
| 14) | Why does total kVA not match the %? Input cell P19 - done
| 15) | correct 12 pulse harmonics - done
| 6) | Note transformer thermal loading |  |  |  |  | not planning on this
170712 | changed 12P table to be same from 10%Z and higher
170713 | created Report tab
special features used: (see Excel Help)
in-cell dropdown
Lists that are used:
Drive_Sel
Filter_Sel
PCC_Sel
Qual_Notes
Source_Sel
TDD_Sel
LinLoad_Sel
data validation
conditional formatting
fixed Report E18
fixed conditional formatting in Input columns G,H
added info in Instructions regarding kVA summation
Called this "LV Harm Est 170713R"
File with harmonics p/w is called "LV Harm Est 170713P"
170801 | Modified Report layout
changed filters to note 7% THDi Filter and 5% THDi Filter
Jesse Stark made the report diagrams dynamic
Fixed a few items in Instructions
170808x | Added G01 as custom harmonic information
a second xfmr on secondary of the main xfmr
on input tab, shows 2 decimal places for hp
170828 | changed wording from % Loaded to Max XFMR Load [%]
hid the custom harmonic tab
disabled the Custom System input selection from Drive_Sel drop-down list
Reordered and updated the Instructions
170912P | Changes made:
Added revision number on first page of report, bottom right
Added rev number to the Instructions and input, first page, top right
corrected instructions rows 124, 126, 139
change contact info at bottom of instructions
removed "none" from the filter drop-down selecton
171002P | Removed AHF input and references in:
Instructions
Input
Report
added eff and pf for calc of hp in quick notes
171019P | Locked cells in the Report
Fixed number of decimal digits in the Report: HP and % Load columns to match Inputs
Modified Instructions - removed motor pf from Adjustable Program Constants
It is no longer being used
Removed note in Instructions stating that groups of drives with same type and filter will have an averaged line cable length
Corrected line 128 in Instructions
171027P | Removed RT to HP converstion on Input
Modified Instructions per removal of RT to HP conversion
Added "Total HP" to Input and Report
180103P | Reworded design checks on Input P6, P7, P8
Added "Design Checks Completed" text on Input P9.
The above show up on the Report
Turned off the gridlines on the tabs
Changed statement on Qual Notes C19
On Report E40 and E44, spelled out Primary and Secondary
On Report E31-34, show % loading and total kVA
Added Thermal tab and result on Input tab as % (est) XFMR Thermal Rating
Expanded some items in Instructions tab
180104P | Removed K-Factor and % (est) XFMR Thermal Rating from Input tab
Hid and locked the 7% and 5% THDi Filter, no load amps values in Instruction tab rows 147,148
180104bP | Changed 'Current' to 'Load Currents' in the Quick View on Input tab
Added note on Instructions tab
180110P | Location of UTILITY on diagram on report tab moved up one cell
Added line 123 to Instructions tab
Moved copy of constants into Drives tab
Added "Passive" to the 7% and 5% THDi Filter labels
Needed to change Drives cells O13, O14, F6:F55
180112P | Added "Input Cable, ft" column to Report page 2
Fills in only if not equal to "" on Input tab
Changed wording in Instructions C287
Changed word in Report F38 to "RESULTS" from "PASS" or "FAIL"
Modified color for cell groups at F38 and M38 on Report tab
|  | Green = 198,224,180 | was 169,208,142
|  | Ping = 255,153,153 | was 255,113,113
Made text in Report M38 bold
Added printing details to Instructions C294 and following
180207P | Created colum AG in the Sum tab and put the triplens there.
This fixed differences in the spectrum and listing with respect to TDD and vTHD
If Max % for transformer is set to 0, don't show design check of Max % being exceeded.
180219P | If %Load = 0, then make drive HP = 0 in Drives tab
Changed wording of "ABB Drives" note in Qual Notes tab
180222P | Show 3ph linear loads on diagrams in Instructions tab.
Added notes to Instructions tab regarding the special notes in the report and the Qual Notes
180228P | Modified "Drives Listed" entry on Qual Notes tab
Changed number of notes drop-downs on Report tab, page 2, from 5 to 6
Reduced the number of free-form notes on Report tab, page 2, from 5 to 4
Modified Instruction tab rows 312-322 correspondingly
The rev level now originates on this tab, K1
Deleted unused tabs:
Harmonic Report
Harmonic Summary
181108P | Changed format of Input D5 to "General" so that a Rev = 1 shows up as "1" instead of a date
190904P | Several changes to add Linear Loads section in Worksheets
Did sum() for h1 to h7
Did sqrt(sumsq()) for h8 to h100
Added parameter in Instructions for xfmr having a delta winding = Y to multiply the PCC1 triplen currents by 0
changed values for DPF in Drives column AH from 0.910
zeroed out AHF data in Power Q4
corrected labels in Instructions regarding drive and filter selections
191210P | corrected sum of Ireal and Ireact in Sum AH to AM
corrected Power W22-27 to get info from Sum AT
corrected Drives BB54 from 'D01'!F1 to 'E01'!F1
moved Input L10:M15 down to L11:M16
replaced harmonics table in E01 with 2002 simulation results using auto-xfmr
modified title in Report E37 to change with Utility or Generator source
| set PF for D01 (12P) to 0.981 |  |  | set D01 E1 to 0
| set PF for E01 (18P) to 0.985 |  |  | set E01 E1 to 0
| set PF for F01 (ULH) to 0.995 |  |  | set F01 E1 to 0
set PCC1 triplen multiplier to 0.05 - seems more realistic
added note in Instructions B334 regarding how harmonics add from different drive/filter combinations
191211P | replaced harmonics table in F01 with 2019 measurement by Peter Wilder
191216P | Modified h5 in F01 table
Modified rule in Drives K for cable length when % Load = 0
Removed result from Input in Drives for future AHF entry
Added Linear Loads in Worksheets
200304P | Moved Linear Loads above drive entry section
Added kVA as another linear load
Changed G11:H11 in Input
Added linear load selection at F14 in Input
Fixed Notes for linear loads
Fixed Instructions per above changes
200305P | Added Analysis info to Instructions
Added kVA load to Report
Made boxes for % Loads vanish if not selected
Changed Conditional formatting for cells that turn red or disappear
200318P | Modified Linear Loads, only two notes for cells
Modified Report to include the linear loads
200319P | In Linear Loads, hid the % Max numbers when grayed out
200407P | Modified wording of note for Input cell E15
200527P | Corrected cells Input C36-C75 as merge and center
200608P | Corrected column G of Drives so when % Load = 0, that drive is not included for calc of avg length of input line length
220705P | Corrected F01 so that Iharm does not vary with % Load

## Relationships (hidden)
Relationships among worksheets
|  |  |  | Drives | Sum | Ann
| Drive Selection | Filter Selection | Code | Row | Column | PF disp
| 6 Pulse w/ No Impedance | none | A01 | 6 | B | 0.99
| 6 Pulse w/ No Impedance | 1.5% AC Reactor | A02 | 7 | C | 0.98
| 6 Pulse w/ No Impedance | 2.5% AC Reactor | A03 | 8 | D | 0.975
| 6 Pulse w/ No Impedance | 3% AC Reactor | A04 | 9 | E | 0.97
| 6 Pulse w/ No Impedance | 5% AC Reactor | A05 | 10 | F | 0.965
| 6 Pulse w/ No Impedance | 7% AC Reactor | A06 | 11 | G | 0.96
| 6 Pulse w/ No Impedance | 10% AC Reactor | A07 | 12 | H | 0.955
| 6 Pulse w/ No Impedance | TCI HG7 Filter | A08 | 13 | I
| 6 Pulse w/ No Impedance | MTE Matrix Filter | A09 | 14 | J
| 6 Pulse w/ 3% DC Choke | none | B01 | 18 | K | 0.98
| 6 Pulse w/ 3% DC Choke | 1.5% AC Reactor | B02 | 19 | L | 0.975
| 6 Pulse w/ 3% DC Choke | 2.5% AC Reactor | B03 | 20 | M | 0.97
| 6 Pulse w/ 3% DC Choke | 3% AC Reactor | B04 | 21 | N | 0.965
| 6 Pulse w/ 3% DC Choke | 5% AC Reactor | B05 | 22 | O | 0.96
| 6 Pulse w/ 3% DC Choke | 7% AC Reactor | B06 | 23 | P | 0.955
| 6 Pulse w/ 3% DC Choke | 10% AC Reactor | B07 | 24 | Q | 0.95
| 6 Pulse w/ 3% DC Choke | TCI HG7 Filter | B08 | 25 | R
| 6 Pulse w/ 3% DC Choke | MTE Matrix Filter | B09 | 26 | S
| 6 Pulse w/ 5% DC Choke | none | C01 | 30 | T | 0.965
| 6 Pulse w/ 5% DC Choke | 1.5% AC Reactor | C02 | 31 | U | 0.965
| 6 Pulse w/ 5% DC Choke | 2.5% AC Reactor | C03 | 32 | V | 0.96
| 6 Pulse w/ 5% DC Choke | 3% AC Reactor | C04 | 33 | W | 0.955
| 6 Pulse w/ 5% DC Choke | 5% AC Reactor | C05 | 34 | X | 0.95
| 6 Pulse w/ 5% DC Choke | 7% AC Reactor | C06 | 35 | Y | 0.95
| 6 Pulse w/ 5% DC Choke | 10% AC Reactor | C07 | 36 | Z | 0.945
| 6 Pulse w/ 5% DC Choke | TCI HG7 Filter | C08 | 37 | AA
| 6 Pulse w/ 5% DC Choke | MTE Matrix Filter | C09 | 38 | AB
| 12 Pulse Drive | none | D01 | 42 | AC | 0.981
| 18 Pulse Drive | none | E01 | 54 | AD | 0.985
| ULH Drive | none | F01 | 66 | AE | 0.995
| A01 to A07 Worksheets | Cell on sheet Ann | From:
| Isc/Iload | C1 | Drives | AZ
| Ifund | H4 | Drives | AQ
| PU Load | J1 | Drives | Y
| PF | N1 |  | fixed number
| A08, A09 Worksheets | Cell on sheet Ann | From :
| Isc/Iload | C1 | Drives | AZ
| A | H1 | Ann | J17
| Ifund | H4 | Ann | J18
| PU Load | J1 | Drives | Y
| rated hp | J4 | Drives | W
| actual hp | J5 | Drives | X
| Ifilter at no load, 100hp | J7 | Drives | N36 for TCI, N37 for MTE
| Ireal at 1pu | J14 | Drives | AM
| PF | N1 | Drives | calc
| Sum Worksheet | row on sheet Sum | From:
| 1 real | 4 | Drives | AN
| 1 react | 5 | Drives | AO
| 1 fund | 6 | Ann | H4
| 2 to 50 | 7 to 55 | Ann | H5 to H53
| Drives Worksheet | column on sheet Drives | From:
| PF disp | AG | Ann | N1
| Ireact | AO | Ann | J12
| Iharm | AP | Ann | H55
| total Iharm | AP3 | Sum | AF107

## A01 (hidden)
A01 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A | 0 | PU Load |  |  | 0.99 | PF
6 Pulse | 6 |  | 1 | 0 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 0.1 | 0.5 | 0.4 | 0 | 0.1
link choke | 1 | 0 | 1 |  |  | 100 | 0 | Ifund
| 2 | 0.017291 | 0.066998 | 0.049707 | 0 | 0.017291 | 0
no line | 3 | 0.55385 | 8.5474 | 7.9935 | 0 | 0.55385 | 0
reactor | 4 | 0.1352 | 0.028695 | -0.10651 | 0 | 0.1352 | 0
| 5 | 93.3687 | 82.8768 | -10.4919 | 0 | 93.3687 | 0
| 6 | 0.068818 | 0.052936 | -0.015882 | 0 | 0.068818 | 0
| 7 | 85.7929 | 65.6754 | -20.1176 | 0 | 85.7929 | 0
| 8 | 0.15207 | 0.052892 | -0.099179 | 0 | 0.15207 | 0
| 9 | 1.1544 | 3.5915 | 2.4371 | 0 | 1.1544 | 0
| 10 | 0.2294 | 0.046741 | -0.18266 | 0 | 0.2294 | 0
| 11 | 69.0486 | 33.6853 | -35.3632 | 0 | 69.0486 | 0
| 12 | 0.043926 | 0.012877 | -0.031049 | 0 | 0.043926 | 0
| 13 | 57.6261 | 19.0088 | -38.6172 | 0 | 57.6261 | 0
| 14 | 0.20927 | 0.055603 | -0.15367 | 0 | 0.20927 | 0
| 15 | 1.1369 | 0.23096 | -0.9059 | 0 | 1.1369 | 0
| 16 | 0.2126 | 0.055251 | -0.15735 | 0 | 0.2126 | 0
| 17 | 38.3059 | 5.3 | -33.0059 | 0 | 38.3059 | 0
| 18 | 0.0068073 | 0.0044855 | -0.0023218 | 0 | 0.0068073 | 0
| 19 | 28.1268 | 5.7694 | -22.3573 | 0 | 28.1268 | 0
| 20 | 0.16228 | 0.034305 | -0.12798 | 0 | 0.16228 | 0
| 21 | 0.62329 | 0.38653 | -0.23676 | 0 | 0.62329 | 0
| 22 | 0.10197 | 0.038702 | -0.063264 | 0 | 0.10197 | 0
| 23 | 14.1113 | 4.5503 | -9.5611 | 0 | 14.1113 | 0
| 24 | 0.036824 | 0.0098383 | -0.026986 | 0 | 0.036824 | 0
| 25 | 9.1461 | 3.3288 | -5.8173 | 0 | 9.1461 | 0
| 26 | 0.050822 | 0.055063 | 0.004241 | 0 | 0.050822 | 0
| 27 | 0.21239 | 0.25707 | 0.044687 | 0 | 0.21239 | 0
| 28 | 0.019393 | 0.047103 | 0.02771 | 0 | 0.019393 | 0
| 29 | 6.5147 | 2.6788 | -3.8359 | 0 | 6.5147 | 0
| 30 | 0.034884 | 0.0041766 | -0.030708 | 0 | 0.034884 | 0
| 31 | 6.3339 | 2.4859 | -3.848 | 0 | 6.3339 | 0
| 32 | 0.046506 | 0.033261 | -0.013246 | 0 | 0.046506 | 0
| 33 | 0.30275 | 0.017217 | -0.28553 | 0 | 0.30275 | 0
| 34 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 35 | 5.903 | 1.4733 | -4.4297 | 0 | 5.903 | 0
| 36 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 37 | 4.7243 | 1.4148 | -3.3095 | 0 | 4.7243 | 0
| 38 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 39 | 0.20799 | 0.13042 | -0.077569 | 0 | 0.20799 | 0
| 40 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 41 | 2.9594 | 1.396 | -1.5633 | 0 | 2.9594 | 0
| 42 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 43 | 2.2179 | 1.1906 | -1.0273 | 0 | 2.2179 | 0
| 44 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 45 | 0.15674 | 0.069136 | -0.087608 | 0 | 0.15674 | 0
| 46 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 47 | 2.3269 | 0.78641 | -1.5404 | 0 | 2.3269 | 0
| 48 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
| 49 | 2.2221 | 0.82313 | -1.399 | 0 | 2.2221 | 0
| 50 | 0.15658 | 0.069206 | -0.087376 | 0 | 0.15658 | 0
[5 empty] | % Ithd | 0 | 0 | Iharm
[5 empty] | % total | 192.0302 | 0 | Itotal
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A02 (hidden)
A02 | Drive row | 38490.0179 | Isc/Iload | 1.5 | 1.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.98 | PF
6 Pulse | 7 |  | 3 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 1 | 2 | 1 | 0.5026 | 1.5026
link choke | 1 | 2 | 3 |  |  | 100 | 0 | Ifund
| 2 | 0.12417 | 0.19165 | 0.067481 | 0.033916 | 0.15808 | 0
1.5% AC | 3 | 4.3858 | 4.8917 | 0.50591 | 0.25427 | 4.64 | 0
reactor | 4 | 0.11238 | 0.12707 | 0.014693 | 0.0073846 | 0.11976 | 0
| 5 | 73.2472 | 60.8315 | -12.4158 | -6.2401 | 67.0071 | 0
| 6 | 0.0070103 | 0.011862 | 0.0048521 | 0.0024386 | 0.0094489 | 0
| 7 | 52.4711 | 34.4739 | -17.9972 | -9.0453 | 43.4258 | 0
| 8 | 0.05704 | 0.019116 | -0.037924 | -0.019061 | 0.03798 | 0
| 9 | 0.66157 | 0.60369 | -0.057878 | -0.02909 | 0.63248 | 0
| 10 | 0.039171 | 0.031896 | -0.0072749 | -0.0036564 | 0.035515 | 0
| 11 | 15.5838 | 6.5636 | -9.0202 | -4.5335 | 11.0503 | 0
| 12 | 0.0045954 | 0.0053292 | 0.00073381 | 0.00036881 | 0.0049642 | 0
| 13 | 6.0811 | 6.4204 | 0.33924 | 0.1705 | 6.2516 | 0
| 14 | 0.040151 | 0.011364 | -0.028787 | -0.014468 | 0.025683 | 0
| 15 | 0.45935 | 0.33979 | -0.11956 | -0.060088 | 0.39926 | 0
| 16 | 0.029549 | 0.019149 | -0.0104 | -0.0052269 | 0.024322 | 0
| 17 | 6.2578 | 3.6516 | -2.6062 | -1.3099 | 4.9479 | 0
| 18 | 0.003708 | 0.0041892 | 0.00048113 | 0.00024182 | 0.0039499 | 0
| 19 | 4.4923 | 2.4618 | -2.0305 | -1.0205 | 3.4718 | 0
| 20 | 0.036035 | 0.013414 | -0.022621 | -0.011369 | 0.024666 | 0
| 21 | 0.28849 | 0.23276 | -0.055723 | -0.028006 | 0.26048 | 0
| 22 | 0.032941 | 0.014397 | -0.018544 | -0.00932 | 0.023621 | 0
| 23 | 2.8173 | 2.0671 | -0.75021 | -0.37705 | 2.4403 | 0
| 24 | 0.0024869 | 0.0037823 | 0.0012954 | 0.00065106 | 0.003138 | 0
| 25 | 2.4769 | 1.4066 | -1.0703 | -0.53794 | 1.939 | 0
| 26 | 0.02657 | 0.017181 | -0.0093891 | -0.004719 | 0.021851 | 0
| 27 | 0.16074 | 0.17381 | 0.013072 | 0.0065701 | 0.16731 | 0
| 28 | 0.028971 | 0.011873 | -0.017099 | -0.0085939 | 0.020378 | 0
| 29 | 1.6107 | 1.3975 | -0.21312 | -0.10712 | 1.5036 | 0
| 30 | 0.0031946 | 0.0036029 | 0.00040831 | 0.00020522 | 0.0033998 | 0
| 31 | 1.4322 | 0.8228 | -0.60942 | -0.30629 | 1.1259 | 0
| 32 | 0.029586 | 0.019536 | -0.01005 | -0.0050513 | 0.024535 | 0
| 33 | 0.12234 | 0.13606 | 0.01372 | 0.0068959 | 0.12923 | 0
| 34 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 35 | 1.2804 | 1.029 | -0.25134 | -0.12632 | 1.154 | 0
| 36 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 37 | 0.86563 | 0.58792 | -0.27771 | -0.13958 | 0.72606 | 0
| 38 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 39 | 0.12948 | 0.11009 | -0.019381 | -0.0097409 | 0.11973 | 0
| 40 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 41 | 0.97885 | 0.76627 | -0.21258 | -0.10684 | 0.87201 | 0
| 42 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 43 | 0.75615 | 0.45363 | -0.30253 | -0.15205 | 0.6041 | 0
| 44 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 45 | 0.11722 | 0.090976 | -0.026243 | -0.01319 | 0.10403 | 0
| 46 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 47 | 0.65684 | 0.58143 | -0.075404 | -0.037898 | 0.61894 | 0
| 48 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
| 49 | 0.54373 | 0.33389 | -0.20984 | -0.10547 | 0.43826 | 0
| 50 | 0.1172 | 0.090951 | -0.026247 | -0.013192 | 0.10401 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 128.89 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A03 (hidden)
A03 | Drive row | 38490.0179 | Isc/Iload | 2.5 | 2.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.975 | PF
6 Pulse | 8 |  | 4 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 2 | 3 | 1 | 0.5026 | 2.5026
link choke | 1 | 3 | 4 |  |  | 100 | 0 | Ifund
| 2 | 0.19165 | 0.032432 | -0.15921 | -0.080021 | 0.11163 | 0
2.5% AC | 3 | 4.8917 | 5.1072 | 0.21557 | 0.10835 | 5 | 0
reactor | 4 | 0.12707 | 0.029674 | -0.097396 | -0.048951 | 0.078118 | 0
| 5 | 60.8315 | 49.3828 | -11.4486 | -5.7541 | 55.0774 | 0
| 6 | 0.011862 | 0.0019223 | -0.0099401 | -0.0049959 | 0.0068665 | 0
| 7 | 34.4739 | 20.7048 | -13.7691 | -6.9203 | 27.5536 | 0
| 8 | 0.019116 | 0.023565 | 0.0044489 | 0.002236 | 0.021352 | 0
| 9 | 0.60369 | 0.42448 | -0.17921 | -0.090071 | 0.51362 | 0
| 10 | 0.031896 | 0.0097073 | -0.022189 | -0.011152 | 0.020744 | 0
| 11 | 6.5636 | 7.6798 | 1.1162 | 0.561 | 7.1246 | 0
| 12 | 0.0053292 | 0.0017456 | -0.0035836 | -0.0018011 | 0.0035281 | 0
| 13 | 6.4204 | 4.0538 | -2.3665 | -1.1894 | 5.2309 | 0
| 14 | 0.011364 | 0.015809 | 0.0044447 | 0.0022339 | 0.013598 | 0
| 15 | 0.33979 | 0.19878 | -0.14102 | -0.070874 | 0.26892 | 0
| 16 | 0.019149 | 0.0088894 | -0.01026 | -0.0051566 | 0.013993 | 0
| 17 | 3.6516 | 3.9361 | 0.28452 | 0.143 | 3.7946 | 0
| 18 | 0.0041892 | 0.0025801 | -0.0016091 | -0.00080874 | 0.0033804 | 0
| 19 | 2.4618 | 1.5612 | -0.90061 | -0.45265 | 2.0092 | 0
| 20 | 0.013414 | 0.013821 | 0.00040619 | 0.00020415 | 0.013619 | 0
| 21 | 0.23276 | 0.12696 | -0.1058 | -0.053176 | 0.17959 | 0
| 22 | 0.014397 | 0.0080433 | -0.0063538 | -0.0031934 | 0.011204 | 0
| 23 | 2.0671 | 2.2928 | 0.22571 | 0.11344 | 2.1805 | 0
| 24 | 0.0037823 | 0.0030036 | -0.00077877 | -0.00039141 | 0.0033909 | 0
| 25 | 1.4066 | 0.98125 | -0.42533 | -0.21377 | 1.1928 | 0
| 26 | 0.017181 | 0.014414 | -0.0027669 | -0.0013907 | 0.01579 | 0
| 27 | 0.17381 | 0.091194 | -0.082616 | -0.041523 | 0.13229 | 0
| 28 | 0.011873 | 0.0069611 | -0.0049114 | -0.0024685 | 0.0094041 | 0
| 29 | 1.3975 | 1.4 | 0.0024512 | 0.0012319 | 1.3988 | 0
| 30 | 0.0036029 | 0.003292 | -0.00031085 | -0.00015623 | 0.0034466 | 0
| 31 | 0.8228 | 0.68512 | -0.13768 | -0.069197 | 0.75361 | 0
| 32 | 0.019536 | 0.014564 | -0.0049722 | -0.002499 | 0.017037 | 0
| 33 | 0.13606 | 0.070763 | -0.065293 | -0.032816 | 0.10324 | 0
| 34 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 35 | 1.029 | 0.95079 | -0.078239 | -0.039323 | 0.9897 | 0
| 36 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 37 | 0.58792 | 0.44571 | -0.14221 | -0.071475 | 0.51645 | 0
| 38 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 39 | 0.11009 | 0.060149 | -0.049945 | -0.025102 | 0.084992 | 0
| 40 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 41 | 0.76627 | 0.64986 | -0.1164 | -0.058505 | 0.70776 | 0
| 42 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 43 | 0.45363 | 0.28528 | -0.16834 | -0.084609 | 0.36902 | 0
| 44 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 45 | 0.090976 | 0.055975 | -0.035001 | -0.017592 | 0.073385 | 0
| 46 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 47 | 0.58143 | 0.44929 | -0.13214 | -0.066415 | 0.51502 | 0
| 48 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
| 49 | 0.33389 | 0.20473 | -0.12916 | -0.064914 | 0.26897 | 0
| 50 | 0.090951 | 0.056069 | -0.034881 | -0.017531 | 0.073419 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 118.0071 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A04 (hidden)
A04 | Drive row | 38490.0179 | Isc/Iload | 3 | 3.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.97 | PF
6 Pulse | 9 |  | 5 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 3 | 4 | 1 | 0.0025981 | 3.0026
link choke | 1 | 4 | 5 |  |  | 100 | 0 | Ifund
| 2 | 0.032432 | 0.026795 | -0.0056374 | -1.4646e-05 | 0.032418 | 0
3% AC | 3 | 5.1072 | 6.2073 | 1.1 | 0.002858 | 5.1101 | 0
reactor | 4 | 0.029674 | 0.021212 | -0.0084614 | -2.1983e-05 | 0.029652 | 0
| 5 | 49.3828 | 41.7275 | -7.6553 | -0.019889 | 49.3629 | 0
| 6 | 0.0019223 | 0.011087 | 0.0091649 | 2.3811e-05 | 0.0019461 | 0
| 7 | 20.7048 | 13.8859 | -6.8189 | -0.017716 | 20.6871 | 0
| 8 | 0.023565 | 0.0085355 | -0.015029 | -3.9048e-05 | 0.023526 | 0
| 9 | 0.42448 | 1.0649 | 0.64042 | 0.0016639 | 0.42614 | 0
| 10 | 0.0097073 | 0.01376 | 0.004053 | 1.053e-05 | 0.0097178 | 0
| 11 | 7.6798 | 7.4571 | -0.22271 | -0.00057863 | 7.6792 | 0
| 12 | 0.0017456 | 0.0061922 | 0.0044466 | 1.1553e-05 | 0.0017571 | 0
| 13 | 4.0538 | 3.1368 | -0.91702 | -0.0023825 | 4.0515 | 0
| 14 | 0.015809 | 0.011301 | -0.0045081 | -1.1712e-05 | 0.015797 | 0
| 15 | 0.19878 | 0.61174 | 0.41296 | 0.0010729 | 0.19985 | 0
| 16 | 0.0088894 | 0.0098005 | 0.00091104 | 2.367e-06 | 0.0088918 | 0
| 17 | 3.9361 | 3.5366 | -0.39955 | -0.0010381 | 3.9351 | 0
| 18 | 0.0025801 | 0.0051323 | 0.0025523 | 6.631e-06 | 0.0025867 | 0
| 19 | 1.5612 | 1.4353 | -0.12586 | -0.00032699 | 1.5609 | 0
| 20 | 0.013821 | 0.012554 | -0.001267 | -3.2918e-06 | 0.013817 | 0
| 21 | 0.12696 | 0.43157 | 0.30461 | 0.0007914 | 0.12775 | 0
| 22 | 0.0080433 | 0.0091411 | 0.0010978 | 2.8523e-06 | 0.0080462 | 0
| 23 | 2.2928 | 1.9472 | -0.34561 | -0.00089791 | 2.2919 | 0
| 24 | 0.0030036 | 0.0053235 | 0.00232 | 6.0275e-06 | 0.0030096 | 0
| 25 | 0.98125 | 0.87517 | -0.10609 | -0.00027563 | 0.98098 | 0
| 26 | 0.014414 | 0.013401 | -0.0010133 | -2.6325e-06 | 0.014411 | 0
| 27 | 0.091194 | 0.33088 | 0.23969 | 0.00062273 | 0.091817 | 0
| 28 | 0.0069611 | 0.0085363 | 0.0015752 | 4.0924e-06 | 0.0069652 | 0
| 29 | 1.4 | 1.0908 | -0.30921 | -0.00080335 | 1.3992 | 0
| 30 | 0.003292 | 0.0050315 | 0.0017395 | 4.5192e-06 | 0.0032965 | 0
| 31 | 0.68512 | 0.58112 | -0.104 | -0.00027021 | 0.68485 | 0
| 32 | 0.014564 | 0.013059 | -0.0015043 | -3.9084e-06 | 0.01456 | 0
| 33 | 0.070763 | 0.26564 | 0.19487 | 0.0005063 | 0.071269 | 0
| 34 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 35 | 0.95079 | 0.68756 | -0.26323 | -0.0006839 | 0.9501 | 0
| 36 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 37 | 0.44571 | 0.35071 | -0.094999 | -0.00024681 | 0.44547 | 0
| 38 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 39 | 0.060149 | 0.2195 | 0.15935 | 0.000414 | 0.060563 | 0
| 40 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 41 | 0.64986 | 0.49479 | -0.15507 | -0.00040289 | 0.64946 | 0
| 42 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 43 | 0.28528 | 0.2178 | -0.067484 | -0.00017533 | 0.28511 | 0
| 44 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 45 | 0.055975 | 0.18455 | 0.12858 | 0.00033405 | 0.056309 | 0
| 46 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 47 | 0.44929 | 0.41294 | -0.036348 | -9.4435e-05 | 0.4492 | 0
| 48 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 49 | 0.20473 | 0.16068 | -0.044051 | -0.00011445 | 0.20462 | 0
| 50 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 113.995 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A05 (hidden)
A05 | Drive row | 38490.0179 | Isc/Iload | 5 | 5.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.965 | PF
6 Pulse | 10 |  | 7 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 5 | 6 | 1 | 0.0025981 | 5.0026
link choke | 1 | 6 | 7 |  |  | 100 | 0 | Ifund
| 2 | 0.010787 | 0.015489 | 0.0047015 | 1.2215e-05 | 0.0108 | 0
5% AC | 3 | 7.7609 | 5.1366 | -2.6243 | -0.0068181 | 7.754 | 0
reactor | 4 | 0.018917 | 0.024592 | 0.0056751 | 1.4744e-05 | 0.018932 | 0
| 5 | 37.2795 | 34.2404 | -3.039 | -0.0078956 | 37.2716 | 0
| 6 | 0.0067285 | 0.0045195 | -0.002209 | -5.7392e-06 | 0.0067228 | 0
| 7 | 10.4074 | 8.4234 | -1.9839 | -0.0051544 | 10.4022 | 0
| 8 | 0.019604 | 0.012637 | -0.0069673 | -1.8102e-05 | 0.019586 | 0
| 9 | 1.5533 | 0.98716 | -0.5661 | -0.0014708 | 1.5518 | 0
| 10 | 0.012351 | 0.0078771 | -0.0044741 | -1.1624e-05 | 0.01234 | 0
| 11 | 6.9056 | 6.5341 | -0.37145 | -0.00096505 | 6.9046 | 0
| 12 | 0.004634 | 0.0012659 | -0.0033681 | -8.7507e-06 | 0.0046253 | 0
| 13 | 3.2688 | 3.1927 | -0.076087 | -0.00019768 | 3.2686 | 0
| 14 | 0.013986 | 0.013727 | -0.00025989 | -6.7522e-07 | 0.013986 | 0
| 15 | 0.77397 | 0.4769 | -0.29708 | -0.00077182 | 0.7732 | 0
| 16 | 0.0093355 | 0.011177 | 0.001841 | 4.783e-06 | 0.0093403 | 0
| 17 | 2.7955 | 2.4617 | -0.33375 | -0.00086711 | 2.7946 | 0
| 18 | 0.0032625 | 0.00097249 | -0.00229 | -5.9495e-06 | 0.0032565 | 0
| 19 | 1.8153 | 1.7533 | -0.061916 | -0.00016086 | 1.8151 | 0
| 20 | 0.011519 | 0.012483 | 0.00096337 | 2.5029e-06 | 0.011522 | 0
| 21 | 0.51233 | 0.3364 | -0.17593 | -0.00045708 | 0.51187 | 0
| 22 | 0.013328 | 0.0099334 | -0.0033949 | -8.8201e-06 | 0.013319 | 0
| 23 | 1.3645 | 1.1709 | -0.19361 | -0.000503 | 1.364 | 0
| 24 | 0.0058117 | 0.0029855 | -0.0028261 | -7.3425e-06 | 0.0058043 | 0
| 25 | 1.0203 | 0.89182 | -0.12849 | -0.00033381 | 1.02 | 0
| 26 | 0.012262 | 0.011494 | -0.00076741 | -1.9938e-06 | 0.01226 | 0
| 27 | 0.40809 | 0.28326 | -0.12483 | -0.00032432 | 0.40777 | 0
| 28 | 0.012557 | 0.010538 | -0.002019 | -5.2455e-06 | 0.012551 | 0
| 29 | 0.75871 | 0.75679 | -0.0019172 | -4.9811e-06 | 0.7587 | 0
| 30 | 0.0046053 | 0.0036992 | -0.00090615 | -2.3542e-06 | 0.004603 | 0
| 31 | 0.56773 | 0.46222 | -0.10551 | -0.00027412 | 0.56745 | 0
| 32 | 0.0088971 | 0.011901 | 0.0030043 | 7.8054e-06 | 0.0089049 | 0
| 33 | 0.34166 | 0.22742 | -0.11423 | -0.00029679 | 0.34136 | 0
| 34 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 35 | 0.51648 | 0.56585 | 0.049367 | 0.00012826 | 0.51661 | 0
| 36 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 37 | 0.34192 | 0.32136 | -0.02056 | -5.3418e-05 | 0.34187 | 0
| 38 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 39 | 0.27641 | 0.17818 | -0.098223 | -0.00025519 | 0.27615 | 0
| 40 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 41 | 0.39951 | 0.41595 | 0.016433 | 4.2693e-05 | 0.39956 | 0
| 42 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 43 | 0.25539 | 0.24819 | -0.0072008 | -1.8708e-05 | 0.25537 | 0
| 44 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 45 | 0.21867 | 0.14808 | -0.070582 | -0.00018338 | 0.21848 | 0
| 46 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 47 | 0.29406 | 0.27869 | -0.015368 | -3.9928e-05 | 0.29402 | 0
| 48 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 49 | 0.19636 | 0.18022 | -0.016136 | -4.1922e-05 | 0.19632 | 0
| 50 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 107.8684 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A06 (hidden)
A06 | Drive row | 38490.0179 | Isc/Iload | 7 | 7.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.96 | PF
6 Pulse | 11 |  | 9 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 7 | 8 | 1 | 0.0025981 | 7.0026
link choke | 1 | 8 | 9 |  |  | 100 | 0 | Ifund
| 2 | 0.011121 | 0.012572 | 0.001451 | 3.7698e-06 | 0.011125 | 0
7% AC | 3 | 3.7115 | 2.8653 | -0.84628 | -0.0021987 | 3.7093 | 0
reactor | 4 | 0.02231 | 0.014672 | -0.0076378 | -1.9843e-05 | 0.02229 | 0
| 5 | 31.8018 | 29.8339 | -1.9679 | -0.0051128 | 31.7967 | 0
| 6 | 0.006017 | 0.007333 | 0.0013161 | 3.4192e-06 | 0.0060204 | 0
| 7 | 7.3447 | 6.8023 | -0.54248 | -0.0014094 | 7.3433 | 0
| 8 | 0.010643 | 0.0043474 | -0.006296 | -1.6357e-05 | 0.010627 | 0
| 9 | 0.68104 | 0.5061 | -0.17494 | -0.0004545 | 0.68059 | 0
| 10 | 0.0066241 | 0.00095446 | -0.0056697 | -1.473e-05 | 0.0066094 | 0
| 11 | 6.0786 | 5.6151 | -0.46349 | -0.0012042 | 6.0774 | 0
| 12 | 0.00072345 | 0.0028138 | 0.0020903 | 5.4308e-06 | 0.00072889 | 0
| 13 | 3.159 | 3.1114 | -0.047592 | -0.00012365 | 3.1589 | 0
| 14 | 0.012923 | 0.0067573 | -0.0061654 | -1.6018e-05 | 0.012907 | 0
| 15 | 0.32445 | 0.24591 | -0.078547 | -0.00020407 | 0.32425 | 0
| 16 | 0.010798 | 0.0049258 | -0.005872 | -1.5256e-05 | 0.010783 | 0
| 17 | 2.1281 | 1.8506 | -0.27754 | -0.00072107 | 2.1274 | 0
| 18 | 0.00053825 | 0.0034208 | 0.0028825 | 7.489e-06 | 0.00054574 | 0
| 19 | 1.6441 | 1.5015 | -0.14261 | -0.00037051 | 1.6438 | 0
| 20 | 0.01066 | 0.0039991 | -0.0066605 | -1.7305e-05 | 0.010642 | 0
| 21 | 0.24976 | 0.20144 | -0.048326 | -0.00012555 | 0.24964 | 0
| 22 | 0.0087777 | 0.0028423 | -0.0059354 | -1.5421e-05 | 0.0087623 | 0
| 23 | 1.045 | 0.98669 | -0.058274 | -0.0001514 | 1.0448 | 0
| 24 | 0.0023273 | 0.0031075 | 0.00078023 | 2.0271e-06 | 0.0023293 | 0
| 25 | 0.77335 | 0.68094 | -0.09241 | -0.00024009 | 0.77311 | 0
| 26 | 0.011502 | 0.0063587 | -0.0051435 | -1.3363e-05 | 0.011489 | 0
| 27 | 0.20564 | 0.15761 | -0.048031 | -0.00012479 | 0.20551 | 0
| 28 | 0.0092931 | 0.003309 | -0.0059841 | -1.5547e-05 | 0.0092775 | 0
| 29 | 0.75576 | 0.72479 | -0.030975 | -8.0475e-05 | 0.75568 | 0
| 30 | 0.0019564 | 0.0028718 | 0.00091535 | 2.3782e-06 | 0.0019588 | 0
| 31 | 0.42487 | 0.43057 | 0.005703 | 1.4817e-05 | 0.42488 | 0
| 32 | 0.011922 | 0.0059188 | -0.0060029 | -1.5596e-05 | 0.011906 | 0
| 33 | 0.15382 | 0.11559 | -0.038227 | -9.9318e-05 | 0.15372 | 0
| 34 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 35 | 0.55172 | 0.48796 | -0.063757 | -0.00016565 | 0.55156 | 0
| 36 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 37 | 0.32334 | 0.31458 | -0.0087615 | -2.2763e-05 | 0.32332 | 0
| 38 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 39 | 0.12256 | 0.098387 | -0.024175 | -6.2807e-05 | 0.1225 | 0
| 40 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 41 | 0.37579 | 0.3244 | -0.051389 | -0.00013351 | 0.37566 | 0
| 42 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 43 | 0.22309 | 0.19779 | -0.025298 | -6.5726e-05 | 0.22302 | 0
| 44 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 45 | 0.10867 | 0.087933 | -0.02074 | -5.3883e-05 | 0.10862 | 0
| 46 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 47 | 0.26697 | 0.26065 | -0.0063268 | -1.6437e-05 | 0.26696 | 0
| 48 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
| 49 | 0.15241 | 0.14568 | -0.0067312 | -1.7488e-05 | 0.15239 | 0
| 50 | 0.10866 | 0.087922 | -0.020735 | -5.3872e-05 | 0.1086 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 105.5311 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A07 (hidden)
A07 | Drive row | 38490.0179 | Isc/Iload | 10 | 10.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.955 | PF
6 Pulse | 12 |  | 11 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
no DC |  | 10 | 12 | 2 | 0.001299 | 10.0026
link choke | 1 | 10 | 11 |  |  | 100 | 0 | Ifund
| 2 | 0.026363 | 0.0039069 | -0.022456 | -2.9171e-05 | 0.026334 | 0
10% AC | 3 | 1.9764 | 1.513 | -0.46344 | -0.00060202 | 1.9758 | 0
reactor | 4 | 0.0034978 | 0.0033184 | -0.00017938 | -2.3302e-07 | 0.0034975 | 0
| 5 | 26.8294 | 24.5244 | -2.3051 | -0.0029944 | 26.8265 | 0
| 6 | 0.0049368 | 0.0021006 | -0.0028362 | -3.6844e-06 | 0.0049331 | 0
| 7 | 6.5167 | 6.6274 | 0.11072 | 0.00014382 | 6.5168 | 0
| 8 | 0.0025416 | 0.0012217 | -0.0013199 | -1.7146e-06 | 0.0025399 | 0
| 9 | 0.31868 | 0.22627 | -0.092415 | -0.00012005 | 0.31856 | 0
| 10 | 0.0059001 | 0.002841 | -0.0030591 | -3.9738e-06 | 0.0058961 | 0
| 11 | 4.7731 | 4.0377 | -0.73537 | -0.00095528 | 4.7722 | 0
| 12 | 0.0033388 | 0.00070415 | -0.0026346 | -3.4225e-06 | 0.0033354 | 0
| 13 | 2.9414 | 2.6891 | -0.25226 | -0.0003277 | 2.9411 | 0
| 14 | 0.0060541 | 0.00088566 | -0.0051685 | -6.714e-06 | 0.0060474 | 0
| 15 | 0.17864 | 0.15239 | -0.026252 | -3.4102e-05 | 0.1786 | 0
| 16 | 0.0015412 | 0.0017707 | 0.00022949 | 2.9812e-07 | 0.0015415 | 0
| 17 | 1.5325 | 1.4252 | -0.10731 | -0.0001394 | 1.5323 | 0
| 18 | 0.0023022 | 0.00071767 | -0.0015845 | -2.0584e-06 | 0.0023002 | 0
| 19 | 1.1979 | 0.96493 | -0.23294 | -0.0003026 | 1.1976 | 0
| 20 | 0.0042899 | 0.0023631 | -0.0019268 | -2.503e-06 | 0.0042874 | 0
| 21 | 0.14886 | 0.11057 | -0.03829 | -4.974e-05 | 0.14881 | 0
| 22 | 0.0017693 | 0.0023684 | 0.00059908 | 7.7823e-07 | 0.0017701 | 0
| 23 | 0.97152 | 0.91499 | -0.056528 | -7.3432e-05 | 0.97145 | 0
| 24 | 0.0016642 | 0.00050466 | -0.0011595 | -1.5063e-06 | 0.0016627 | 0
| 25 | 0.60411 | 0.59625 | -0.0078562 | -1.0206e-05 | 0.6041 | 0
| 26 | 0.0057283 | 0.0014156 | -0.0043127 | -5.6024e-06 | 0.0057227 | 0
| 27 | 0.099377 | 0.075392 | -0.023985 | -3.1158e-05 | 0.099346 | 0
| 28 | 0.0008443 | 0.0017537 | 0.00090938 | 1.1813e-06 | 0.00084548 | 0
| 29 | 0.61841 | 0.50579 | -0.11262 | -0.0001463 | 0.61826 | 0
| 30 | 0.0026822 | 0.00053985 | -0.0021423 | -2.783e-06 | 0.0026794 | 0
| 31 | 0.43268 | 0.37618 | -0.056505 | -7.3402e-05 | 0.43261 | 0
| 32 | 0.0045875 | 0.00127 | -0.0033175 | -4.3096e-06 | 0.0045832 | 0
| 33 | 0.084151 | 0.067504 | -0.016648 | -2.1626e-05 | 0.08413 | 0
| 34 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 35 | 0.39029 | 0.36343 | -0.026859 | -3.489e-05 | 0.39026 | 0
| 36 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 37 | 0.26039 | 0.23294 | -0.027452 | -3.5662e-05 | 0.26035 | 0
| 38 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 39 | 0.071958 | 0.051367 | -0.020591 | -2.6749e-05 | 0.071931 | 0
| 40 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 41 | 0.3053 | 0.27286 | -0.032442 | -4.2144e-05 | 0.30526 | 0
| 42 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 43 | 0.1877 | 0.18025 | -0.0074551 | -9.6844e-06 | 0.18769 | 0
| 44 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 45 | 0.058262 | 0.044255 | -0.014007 | -1.8195e-05 | 0.058243 | 0
| 46 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 47 | 0.23679 | 0.19038 | -0.046409 | -6.0287e-05 | 0.23673 | 0
| 48 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 49 | 0.14317 | 0.11821 | -0.024956 | -3.2419e-05 | 0.14313 | 0
| 50 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 103.9411 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## A08 (hidden)
A08 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A | 0 | PU Load |  |  | 0.995 | PF | kW/kVA
6 Pulse | 13 |  | 1 | 0 |  |  |  |  | 0.1475 | Harmonic multiplier
no DC |  | 0.1 | 0.5 | 0.4 | 0 | 0.1 | [6 empty] | -0.099875 | QF | kVAR/kVA
link choke | 1 | 0 | 1 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.32933 | 0.31535 | -0.013978 | 0 | 0.32933 | 0 |  | 0 | actual hp
7% THDi | 3 | 0.04526 | 0.043339 | -0.001921 | 0 | 0.04526 | 0
filter | 4 | 0.29726 | 0.28464 | -0.012617 | 0 | 0.29726 | 0 |  | -35 | Ifilter at no load, 100hp
| 5 | 5.261 | 5.0377 | -0.2233 | 0 | 5.261 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.020329 | 0.019466 | -0.00086281 | 0 | 0.020329 | 0
| 7 | 3.7605 | 3.6009 | -0.15961 | 0 | 3.7605 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.019663 | 0.018829 | -0.00083458 | 0 | 0.019663 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.0096151 | 0.009207 | -0.0004081 | 0 | 0.0096151 | 0 |  | 0 | Ireact at xpu |  |  |  | PU Load | Harm Mult | J24 | J2 | eqn
| 10 | 0.0054136 | 0.0051838 | -0.00022977 | 0 | 0.0054136 | 0 | [6 empty] | 1 | 1 | 7.57 | 1 | 1
| 11 | 3.4945 | 3.3462 | -0.14832 | 0 | 3.4945 | 0 |  | 0 | Ireal at 1pu | = Irated |  |  | 0.8 | 1.06 | 8.0242 | 0.839 | 0.8295
| 12 | 0.0033849 | 0.0032412 | -0.00014367 | 0 | 0.0033849 | 0 |  | 0 | Ireal at xpu |  |  |  | 0.6 | 1.104 | 8.3573 | 0.661 | 0.659
| 13 | 2.2521 | 2.1565 | -0.095585 | 0 | 2.2521 | 0 | [6 empty] | 0.4 | 1.132 | 8.5692 | 0.491 | 0.4885
| 14 | 0.012004 | 0.011495 | -0.00050949 | 0 | 0.012004 | 0 |  | 0 | Ifund at 1pu |  |  |  | 0.2 | 1.144 | 8.6601 |  | 0.318
| 15 | 0.0022368 | 0.0021419 | -9.4938e-05 | 0 | 0.0022368 | 0 |  | 0 | Ifund at xpu
| 16 | 0.010046 | 0.0096194 | -0.00042638 | 0 | 0.010046 | 0
| 17 | 1.1226 | 1.075 | -0.047647 | 0 | 1.1226 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0029975 | 0.0028703 | -0.00012723 | 0 | 0.0029975 | 0
| 19 | 1.0549 | 1.0101 | -0.044772 | 0 | 1.0549 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0039537 | 0.0037859 | -0.00016781 | 0 | 0.0039537 | 0
| 21 | 0.0017776 | 0.0017022 | -7.5449e-05 | 0 | 0.0017776 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0060108 | 0.0057557 | -0.00025512 | 0 | 0.0060108 | 0
| 23 | 0.62977 | 0.60304 | -0.026729 | 0 | 0.62977 | 0
| 24 | 0.00084787 | 0.00081188 | -3.5986e-05 | 0 | 0.00084787 | 0
| 25 | 0.50563 | 0.48417 | -0.021461 | 0 | 0.50563 | 0
| 26 | 0.0043441 | 0.0041597 | -0.00018438 | 0 | 0.0043441 | 0
| 27 | 0.0016681 | 0.0015973 | -7.0798e-05 | 0 | 0.0016681 | 0
| 28 | 0.0026594 | 0.0025465 | -0.00011287 | 0 | 0.0026594 | 0
| 29 | 0.45607 | 0.43671 | -0.019357 | 0 | 0.45607 | 0
| 30 | 0.0013184 | 0.0012624 | -5.5956e-05 | 0 | 0.0013184 | 0
| 31 | 0.37522 | 0.3593 | -0.015926 | 0 | 0.37522 | 0
| 32 | 0.0044425 | 0.0042539 | -0.00018855 | 0 | 0.0044425 | 0
| 33 | 0.00039151 | 0.0003749 | -1.6617e-05 | 0 | 0.00039151 | 0
| 34 | 0.0043909 | 0.0042045 | -0.00018636 | 0 | 0.0043909 | 0
| 35 | 0.28137 | 0.26943 | -0.011942 | 0 | 0.28137 | 0
| 36 | 0.001004 | 0.0009614 | -4.2614e-05 | 0 | 0.001004 | 0
| 37 | 0.27092 | 0.25942 | -0.011499 | 0 | 0.27092 | 0
| 38 | 0.0018623 | 0.0017832 | -7.9041e-05 | 0 | 0.0018623 | 0
| 39 | 0.001057 | 0.0010121 | -4.4863e-05 | 0 | 0.001057 | 0
| 40 | 0.0025154 | 0.0024086 | -0.00010676 | 0 | 0.0025154 | 0
| 41 | 0.20192 | 0.19335 | -0.0085701 | 0 | 0.20192 | 0
| 42 | 0.0003834 | 0.00036713 | -1.6273e-05 | 0 | 0.0003834 | 0
| 43 | 0.17961 | 0.17199 | -0.0076234 | 0 | 0.17961 | 0
| 44 | 0.0029536 | 0.0028282 | -0.00012536 | 0 | 0.0029536 | 0
| 45 | 0.00056241 | 0.00053854 | -2.3871e-05 | 0 | 0.00056241 | 0
| 46 | 0.0022562 | 0.0021605 | -9.5763e-05 | 0 | 0.0022562 | 0
| 47 | 0.1691 | 0.16192 | -0.007177 | 0 | 0.1691 | 0
| 48 | 0.00080287 | 0.00076879 | -3.4076e-05 | 0 | 0.00080287 | 0
| 49 | 0.14794 | 0.14166 | -0.0062791 | 0 | 0.14794 | 0
| 50 | 0.0022559 | 0.0021602 | -9.575e-05 | 0 | 0.0022559 | 0
[5 empty] | thd | 7.9343 | 0 | Iharm
[5 empty] | total | 100.3143 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.32933 | 0.31535 | 0.30142 | 0.28744 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862
3 |  |  | 0.04526 | 0.043339 | 0.041423 | 0.039502 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331
4 |  |  | 0.29726 | 0.28464 | 0.27206 | 0.25945 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832
5 |  |  | 5.261 | 5.0377 | 4.8151 | 4.5918 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719
6 |  |  | 0.020329 | 0.019466 | 0.018605 | 0.017743 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666
7 |  |  | 3.7605 | 3.6009 | 3.4418 | 3.2822 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679
8 |  |  | 0.019663 | 0.018829 | 0.017997 | 0.017162 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088
9 |  |  | 0.0096151 | 0.009207 | 0.0088001 | 0.008392 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557
10 |  |  | 0.0054136 | 0.0051838 | 0.0049547 | 0.004725 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045
11 |  |  | 3.4945 | 3.3462 | 3.1983 | 3.05 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368
12 |  |  | 0.0033849 | 0.0032412 | 0.003098 | 0.0029543 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416
13 |  |  | 2.2521 | 2.1565 | 2.0612 | 1.9656 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571
14 |  |  | 0.012004 | 0.011495 | 0.010987 | 0.010477 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432
15 |  |  | 0.0022368 | 0.0021419 | 0.0020472 | 0.0019523 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438
16 |  |  | 0.010046 | 0.0096194 | 0.0091943 | 0.0087679 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873
17 |  |  | 1.1226 | 1.075 | 1.0275 | 0.97981 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557
18 |  |  | 0.0029975 | 0.0028703 | 0.0027435 | 0.0026162 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049
19 |  |  | 1.0549 | 1.0101 | 0.96545 | 0.92068 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669
20 |  |  | 0.0039537 | 0.0037859 | 0.0036186 | 0.0034508 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359
21 |  |  | 0.0017776 | 0.0017022 | 0.001627 | 0.0015515 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448
22 |  |  | 0.0060108 | 0.0057557 | 0.0055013 | 0.0052462 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235
23 |  |  | 0.62977 | 0.60304 | 0.57639 | 0.54966 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728
24 |  |  | 0.00084787 | 0.00081188 | 0.000776 | 0.00074001 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681
25 |  |  | 0.50563 | 0.48417 | 0.46277 | 0.44131 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394
26 |  |  | 0.0043441 | 0.0041597 | 0.0039759 | 0.0037915 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751
27 |  |  | 0.0016681 | 0.0015973 | 0.0015267 | 0.0014559 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496
28 |  |  | 0.0026594 | 0.0025465 | 0.002434 | 0.0023211 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311
29 |  |  | 0.45607 | 0.43671 | 0.41741 | 0.39805 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633
30 |  |  | 0.0013184 | 0.0012624 | 0.0012066 | 0.0011507 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457
31 |  |  | 0.37522 | 0.3593 | 0.34342 | 0.32749 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608
32 |  |  | 0.0044425 | 0.0042539 | 0.0040659 | 0.0038774 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606
33 |  |  | 0.00039151 | 0.0003749 | 0.00035833 | 0.00034171 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023
34 |  |  | 0.0043909 | 0.0042045 | 0.0040187 | 0.0038323 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157
35 |  |  | 0.28137 | 0.26943 | 0.25752 | 0.24558 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452
36 |  |  | 0.001004 | 0.0009614 | 0.00091891 | 0.0008763 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725
37 |  |  | 0.27092 | 0.25942 | 0.24796 | 0.23646 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543
38 |  |  | 0.0018623 | 0.0017832 | 0.0017044 | 0.0016254 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183
39 |  |  | 0.001057 | 0.0010121 | 0.00096741 | 0.00092255 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856
40 |  |  | 0.0025154 | 0.0024086 | 0.0023021 | 0.0021954 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859
41 |  |  | 0.20192 | 0.19335 | 0.1848 | 0.17623 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547
42 |  |  | 0.0003834 | 0.00036713 | 0.0003509 | 0.00033463 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318
43 |  |  | 0.17961 | 0.17199 | 0.16439 | 0.15677 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609
44 |  |  | 0.0029536 | 0.0028282 | 0.0027032 | 0.0025779 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667
45 |  |  | 0.00056241 | 0.00053854 | 0.00051474 | 0.00049087 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875
46 |  |  | 0.0022562 | 0.0021605 | 0.002065 | 0.0019692 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607
47 |  |  | 0.1691 | 0.16192 | 0.15476 | 0.14759 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695
48 |  |  | 0.00080287 | 0.00076879 | 0.00073482 | 0.00070074 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771
49 |  |  | 0.14794 | 0.14166 | 0.1354 | 0.12912 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856
50 |  |  | 0.0022559 | 0.0021602 | 0.0020647 | 0.001969 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605
| Ithd |  | 7.9343 | 7.5976 | 7.2618 | 6.9251 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951

## A09 (hidden)
A09 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A | 0 | PU Load |  |  | 0.999 | PF | kW/kVA
6 Pulse | 14 |  | 1 | 0 |  |  |  |  | 1.1251 | Harmonic multiplier
no DC |  | 0.1 | 0.5 | 0.4 | 0 | 0.1 | [6 empty] | 0.04471 | QF | kVAR/kVA
link choke | 1 | 0 | 1 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.20697 | 0.20519 | -0.0017835 | 0 | 0.20697 | 0 |  | 0 | actual hp
5% THDi | 3 | 0.028444 | 0.028199 | -0.00024511 | 0 | 0.028444 | 0
filter | 4 | 0.18682 | 0.18521 | -0.0016098 | 0 | 0.18682 | 0 |  | -40 | Ifilter at no load, 100hp
| 5 | 3.3064 | 3.2779 | -0.028492 | 0 | 3.3064 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.012776 | 0.012666 | -0.00011009 | 0 | 0.012776 | 0
| 7 | 2.3633 | 2.343 | -0.020365 | 0 | 2.3633 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.012358 | 0.012251 | -0.00010649 | 0 | 0.012358 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.0060427 | 0.0059906 | -5.2072e-05 | 0 | 0.0060427 | 0 |  | 0 | Ireact at xpu |  |  |  | PU Load | Harm Mult | J24 | J2 | eqn
| 10 | 0.0034023 | 0.0033729 | -2.9318e-05 | 0 | 0.0034023 | 0 | [6 empty] | 1 | 1 | 4.94 | 1 | 1
| 11 | 2.1962 | 2.1773 | -0.018925 | 0 | 2.1962 | 0 |  | 0 | Ireal at 1pu |  |  |  | 0.8 | 1.06 | 5.2364 | 1.059 | 1.058
| 12 | 0.0021273 | 0.002109 | -1.8331e-05 | 0 | 0.0021273 | 0 |  | 0 | Ireal at xpu |  |  |  | 0.6 | 1.104 | 5.4538 | 1.099 | 1.0996
| 13 | 1.4153 | 1.4031 | -0.012196 | 0 | 1.4153 | 0 | [6 empty] | 0.4 | 1.132 | 5.5921 | 1.125 | 1.1246
| 14 | 0.0075441 | 0.0074791 | -6.5009e-05 | 0 | 0.0075441 | 0 |  | 0 | Ifund at 1pu |  |  |  | 0.2 | 1.144 | 5.6514 |  | 1.1331
| 15 | 0.0014058 | 0.0013936 | -1.2114e-05 | 0 | 0.0014058 | 0 |  | 0 | Ifund at xpu
| 16 | 0.0063134 | 0.006259 | -5.4404e-05 | 0 | 0.0063134 | 0
| 17 | 0.70552 | 0.69944 | -0.0060796 | 0 | 0.70552 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0018838 | 0.0018676 | -1.6233e-05 | 0 | 0.0018838 | 0
| 19 | 0.66294 | 0.65723 | -0.0057127 | 0 | 0.66294 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0024848 | 0.0024634 | -2.1412e-05 | 0 | 0.0024848 | 0
| 21 | 0.0011172 | 0.0011075 | -9.627e-06 | 0 | 0.0011172 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0037776 | 0.003745 | -3.2552e-05 | 0 | 0.0037776 | 0
| 23 | 0.39579 | 0.39238 | -0.0034106 | 0 | 0.39579 | 0
| 24 | 0.00053285 | 0.00052826 | -4.5917e-06 | 0 | 0.00053285 | 0
| 25 | 0.31777 | 0.31503 | -0.0027383 | 0 | 0.31777 | 0
| 26 | 0.0027301 | 0.0027066 | -2.3526e-05 | 0 | 0.0027301 | 0
| 27 | 0.0010483 | 0.0010393 | -9.0336e-06 | 0 | 0.0010483 | 0
| 28 | 0.0016713 | 0.0016569 | -1.4402e-05 | 0 | 0.0016713 | 0
| 29 | 0.28662 | 0.28415 | -0.0024699 | 0 | 0.28662 | 0
| 30 | 0.00082855 | 0.00082141 | -7.1398e-06 | 0 | 0.00082855 | 0
| 31 | 0.23581 | 0.23378 | -0.0020321 | 0 | 0.23581 | 0
| 32 | 0.0027919 | 0.0027679 | -2.4059e-05 | 0 | 0.0027919 | 0
| 33 | 0.00024605 | 0.00024393 | -2.1203e-06 | 0 | 0.00024605 | 0
| 34 | 0.0027595 | 0.0027357 | -2.3779e-05 | 0 | 0.0027595 | 0
| 35 | 0.17683 | 0.17531 | -0.0015238 | 0 | 0.17683 | 0
| 36 | 0.00063098 | 0.00062555 | -5.4373e-06 | 0 | 0.00063098 | 0
| 37 | 0.17026 | 0.1688 | -0.0014672 | 0 | 0.17026 | 0
| 38 | 0.0011704 | 0.0011603 | -1.0085e-05 | 0 | 0.0011704 | 0
| 39 | 0.00066429 | 0.00065857 | -5.7243e-06 | 0 | 0.00066429 | 0
| 40 | 0.0015808 | 0.0015672 | -1.3622e-05 | 0 | 0.0015808 | 0
| 41 | 0.1269 | 0.12581 | -0.0010935 | 0 | 0.1269 | 0
| 42 | 0.00024095 | 0.00023888 | -2.0764e-06 | 0 | 0.00024095 | 0
| 43 | 0.11288 | 0.11191 | -0.00097272 | 0 | 0.11288 | 0
| 44 | 0.0018562 | 0.0018402 | -1.5996e-05 | 0 | 0.0018562 | 0
| 45 | 0.00035346 | 0.00035041 | -3.0458e-06 | 0 | 0.00035346 | 0
| 46 | 0.001418 | 0.0014057 | -1.2219e-05 | 0 | 0.001418 | 0
| 47 | 0.10627 | 0.10536 | -0.00091577 | 0 | 0.10627 | 0
| 48 | 0.00050457 | 0.00050023 | -4.348e-06 | 0 | 0.00050457 | 0
| 49 | 0.092976 | 0.092175 | -0.00080119 | 0 | 0.092976 | 0
| 50 | 0.0014178 | 0.0014056 | -1.2217e-05 | 0 | 0.0014178 | 0
[5 empty] | thd | 4.9864 | 0 | Iharm
[5 empty] | total | 100.1242 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.20697 | 0.20519 | 0.20336 | 0.20158 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034
3 |  |  | 0.028444 | 0.028199 | 0.027948 | 0.027703 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532
4 |  |  | 0.18682 | 0.18521 | 0.18356 | 0.18195 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083
5 |  |  | 3.3064 | 3.2779 | 3.2487 | 3.2202 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003
6 |  |  | 0.012776 | 0.012666 | 0.012553 | 0.012443 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366
7 |  |  | 2.3633 | 2.343 | 2.3221 | 2.3018 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876
8 |  |  | 0.012358 | 0.012251 | 0.012142 | 0.012036 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961
9 |  |  | 0.0060427 | 0.0059906 | 0.0059374 | 0.0058853 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849
10 |  |  | 0.0034023 | 0.0033729 | 0.0033429 | 0.0033136 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932
11 |  |  | 2.1962 | 2.1773 | 2.1579 | 2.139 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258
12 |  |  | 0.0021273 | 0.002109 | 0.0020902 | 0.0020719 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591
13 |  |  | 1.4153 | 1.4031 | 1.3907 | 1.3785 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37
14 |  |  | 0.0075441 | 0.0074791 | 0.0074125 | 0.0073475 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022
15 |  |  | 0.0014058 | 0.0013936 | 0.0013812 | 0.0013691 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607
16 |  |  | 0.0063134 | 0.006259 | 0.0062033 | 0.0061489 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111
17 |  |  | 0.70552 | 0.69944 | 0.69322 | 0.68714 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829
18 |  |  | 0.0018838 | 0.0018676 | 0.001851 | 0.0018348 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234
19 |  |  | 0.66294 | 0.65723 | 0.65138 | 0.64567 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169
20 |  |  | 0.0024848 | 0.0024634 | 0.0024415 | 0.00242 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051
21 |  |  | 0.0011172 | 0.0011075 | 0.0010977 | 0.0010881 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814
22 |  |  | 0.0037776 | 0.003745 | 0.0037117 | 0.0036791 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564
23 |  |  | 0.39579 | 0.39238 | 0.38889 | 0.38548 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831
24 |  |  | 0.00053285 | 0.00052826 | 0.00052356 | 0.00051897 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577
25 |  |  | 0.31777 | 0.31503 | 0.31223 | 0.30949 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758
26 |  |  | 0.0027301 | 0.0027066 | 0.0026825 | 0.002659 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426
27 |  |  | 0.0010483 | 0.0010393 | 0.00103 | 0.001021 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147
28 |  |  | 0.0016713 | 0.0016569 | 0.0016422 | 0.0016278 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177
29 |  |  | 0.28662 | 0.28415 | 0.28163 | 0.27916 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743
30 |  |  | 0.00082855 | 0.00082141 | 0.0008141 | 0.00080696 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198
31 |  |  | 0.23581 | 0.23378 | 0.2317 | 0.22967 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825
32 |  |  | 0.0027919 | 0.0027679 | 0.0027432 | 0.0027192 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024
33 |  |  | 0.00024605 | 0.00024393 | 0.00024176 | 0.00023964 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816
34 |  |  | 0.0027595 | 0.0027357 | 0.0027114 | 0.0026876 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671
35 |  |  | 0.17683 | 0.17531 | 0.17375 | 0.17222 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116
36 |  |  | 0.00063098 | 0.00062555 | 0.00061998 | 0.00061454 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075
37 |  |  | 0.17026 | 0.1688 | 0.16729 | 0.16583 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648
38 |  |  | 0.0011704 | 0.0011603 | 0.00115 | 0.0011399 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328
39 |  |  | 0.00066429 | 0.00065857 | 0.00065271 | 0.00064698 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299
40 |  |  | 0.0015808 | 0.0015672 | 0.0015532 | 0.0015396 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301
41 |  |  | 0.1269 | 0.12581 | 0.12469 | 0.12359 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283
42 |  |  | 0.00024095 | 0.00023888 | 0.00023675 | 0.00023468 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323
43 |  |  | 0.11288 | 0.11191 | 0.11091 | 0.10994 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926
44 |  |  | 0.0018562 | 0.0018402 | 0.0018239 | 0.0018079 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967
45 |  |  | 0.00035346 | 0.00035041 | 0.00034729 | 0.00034425 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212
46 |  |  | 0.001418 | 0.0014057 | 0.0013932 | 0.001381 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725
47 |  |  | 0.10627 | 0.10536 | 0.10442 | 0.1035 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286
48 |  |  | 0.00050457 | 0.00050023 | 0.00049578 | 0.00049143 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884
49 |  |  | 0.092976 | 0.092175 | 0.091355 | 0.090554 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995
50 |  |  | 0.0014178 | 0.0014056 | 0.0013931 | 0.0013808 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723
| Ithd |  | 4.9864 | 4.9435 | 4.8995 | 4.8565 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266

## B01 (hidden)
B01 | Drive row | 38490.0179 | Isc/Iload | 3 | 3.0026 | %Z | 0 | A | 0 | PU Load |  |  | 0.98 | PF
6 Pulse | 18 |  | 5 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 3 | 4 | 1 | 0.0025981 | 3.0026
link choke | 1 | 4 | 5 |  |  | 100 | 0 | Ifund
| 2 | 0.032432 | 0.026795 | -0.0056374 | -1.4646e-05 | 0.032418 | 0
no line | 3 | 5.1072 | 6.2073 | 1.1 | 0.002858 | 5.1101 | 0
reactor | 4 | 0.029674 | 0.021212 | -0.0084614 | -2.1983e-05 | 0.029652 | 0
| 5 | 49.3828 | 41.7275 | -7.6553 | -0.019889 | 49.3629 | 0
| 6 | 0.0019223 | 0.011087 | 0.0091649 | 2.3811e-05 | 0.0019461 | 0
| 7 | 20.7048 | 13.8859 | -6.8189 | -0.017716 | 20.6871 | 0
| 8 | 0.023565 | 0.0085355 | -0.015029 | -3.9048e-05 | 0.023526 | 0
| 9 | 0.42448 | 1.0649 | 0.64042 | 0.0016639 | 0.42614 | 0
| 10 | 0.0097073 | 0.01376 | 0.004053 | 1.053e-05 | 0.0097178 | 0
| 11 | 7.6798 | 7.4571 | -0.22271 | -0.00057863 | 7.6792 | 0
| 12 | 0.0017456 | 0.0061922 | 0.0044466 | 1.1553e-05 | 0.0017571 | 0
| 13 | 4.0538 | 3.1368 | -0.91702 | -0.0023825 | 4.0515 | 0
| 14 | 0.015809 | 0.011301 | -0.0045081 | -1.1712e-05 | 0.015797 | 0
| 15 | 0.19878 | 0.61174 | 0.41296 | 0.0010729 | 0.19985 | 0
| 16 | 0.0088894 | 0.0098005 | 0.00091104 | 2.367e-06 | 0.0088918 | 0
| 17 | 3.9361 | 3.5366 | -0.39955 | -0.0010381 | 3.9351 | 0
| 18 | 0.0025801 | 0.0051323 | 0.0025523 | 6.631e-06 | 0.0025867 | 0
| 19 | 1.5612 | 1.4353 | -0.12586 | -0.00032699 | 1.5609 | 0
| 20 | 0.013821 | 0.012554 | -0.001267 | -3.2918e-06 | 0.013817 | 0
| 21 | 0.12696 | 0.43157 | 0.30461 | 0.0007914 | 0.12775 | 0
| 22 | 0.0080433 | 0.0091411 | 0.0010978 | 2.8523e-06 | 0.0080462 | 0
| 23 | 2.2928 | 1.9472 | -0.34561 | -0.00089791 | 2.2919 | 0
| 24 | 0.0030036 | 0.0053235 | 0.00232 | 6.0275e-06 | 0.0030096 | 0
| 25 | 0.98125 | 0.87517 | -0.10609 | -0.00027563 | 0.98098 | 0
| 26 | 0.014414 | 0.013401 | -0.0010133 | -2.6325e-06 | 0.014411 | 0
| 27 | 0.091194 | 0.33088 | 0.23969 | 0.00062273 | 0.091817 | 0
| 28 | 0.0069611 | 0.0085363 | 0.0015752 | 4.0924e-06 | 0.0069652 | 0
| 29 | 1.4 | 1.0908 | -0.30921 | -0.00080335 | 1.3992 | 0
| 30 | 0.003292 | 0.0050315 | 0.0017395 | 4.5192e-06 | 0.0032965 | 0
| 31 | 0.68512 | 0.58112 | -0.104 | -0.00027021 | 0.68485 | 0
| 32 | 0.014564 | 0.013059 | -0.0015043 | -3.9084e-06 | 0.01456 | 0
| 33 | 0.070763 | 0.26564 | 0.19487 | 0.0005063 | 0.071269 | 0
| 34 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 35 | 0.95079 | 0.68756 | -0.26323 | -0.0006839 | 0.9501 | 0
| 36 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 37 | 0.44571 | 0.35071 | -0.094999 | -0.00024681 | 0.44547 | 0
| 38 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 39 | 0.060149 | 0.2195 | 0.15935 | 0.000414 | 0.060563 | 0
| 40 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 41 | 0.64986 | 0.49479 | -0.15507 | -0.00040289 | 0.64946 | 0
| 42 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 43 | 0.28528 | 0.2178 | -0.067484 | -0.00017533 | 0.28511 | 0
| 44 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 45 | 0.055975 | 0.18455 | 0.12858 | 0.00033405 | 0.056309 | 0
| 46 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 47 | 0.44929 | 0.41294 | -0.036348 | -9.4435e-05 | 0.4492 | 0
| 48 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
| 49 | 0.20473 | 0.16068 | -0.044051 | -0.00011445 | 0.20462 | 0
| 50 | 0.056069 | 0.18458 | 0.12851 | 0.00033387 | 0.056403 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 113.995 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B02 (hidden)
B02 | Drive row | 38490.0179 | Isc/Iload | 4.5 | 4.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.975 | PF
6 Pulse | 19 |  | 6 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 4 | 5 | 1 | 0.5026 | 4.5026
link choke | 1 | 5 | 6 |  |  | 100 | 0 | Ifund
| 2 | 0.026795 | 0.010787 | -0.016008 | -0.0080454 | 0.01875 | 0
1.5% AC | 3 | 6.2073 | 7.7609 | 1.5536 | 0.78082 | 6.9881 | 0
reactor | 4 | 0.021212 | 0.018917 | -0.0022955 | -0.0011537 | 0.020059 | 0
| 5 | 41.7275 | 37.2795 | -4.4481 | -2.2356 | 39.4919 | 0
| 6 | 0.011087 | 0.0067285 | -0.0043586 | -0.0021906 | 0.0088965 | 0
| 7 | 13.8859 | 10.4074 | -3.4786 | -1.7483 | 12.1376 | 0
| 8 | 0.0085355 | 0.019604 | 0.011068 | 0.005563 | 0.014098 | 0
| 9 | 1.0649 | 1.5533 | 0.48837 | 0.24545 | 1.3103 | 0
| 10 | 0.01376 | 0.012351 | -0.0014091 | -0.00070822 | 0.013052 | 0
| 11 | 7.4571 | 6.9056 | -0.55152 | -0.27719 | 7.1799 | 0
| 12 | 0.0061922 | 0.004634 | -0.0015582 | -0.00078315 | 0.0054091 | 0
| 13 | 3.1368 | 3.2688 | 0.13197 | 0.06633 | 3.2031 | 0
| 14 | 0.011301 | 0.013986 | 0.0026859 | 0.0013499 | 0.01265 | 0
| 15 | 0.61174 | 0.77397 | 0.16224 | 0.08154 | 0.69328 | 0
| 16 | 0.0098005 | 0.0093355 | -0.00046494 | -0.00023368 | 0.0095668 | 0
| 17 | 3.5366 | 2.7955 | -0.74109 | -0.37247 | 3.1641 | 0
| 18 | 0.0051323 | 0.0032625 | -0.0018699 | -0.0009398 | 0.0041925 | 0
| 19 | 1.4353 | 1.8153 | 0.37991 | 0.19094 | 1.6263 | 0
| 20 | 0.012554 | 0.011519 | -0.0010344 | -0.0005199 | 0.012034 | 0
| 21 | 0.43157 | 0.51233 | 0.08076 | 0.04059 | 0.47216 | 0
| 22 | 0.0091411 | 0.013328 | 0.0041871 | 0.0021045 | 0.011246 | 0
| 23 | 1.9472 | 1.3645 | -0.58269 | -0.29286 | 1.6543 | 0
| 24 | 0.0053235 | 0.0058117 | 0.00048813 | 0.00024533 | 0.0055689 | 0
| 25 | 0.87517 | 1.0203 | 0.14514 | 0.072947 | 0.94811 | 0
| 26 | 0.013401 | 0.012262 | -0.0011388 | -0.00057238 | 0.012828 | 0
| 27 | 0.33088 | 0.40809 | 0.077208 | 0.038805 | 0.36969 | 0
| 28 | 0.0085363 | 0.012557 | 0.0040204 | 0.0020206 | 0.010557 | 0
| 29 | 1.0908 | 0.75871 | -0.33208 | -0.1669 | 0.92388 | 0
| 30 | 0.0050315 | 0.0046053 | -0.00042618 | -0.0002142 | 0.0048173 | 0
| 31 | 0.58112 | 0.56773 | -0.013393 | -0.0067311 | 0.57439 | 0
| 32 | 0.013059 | 0.0088971 | -0.0041622 | -0.0020919 | 0.010967 | 0
| 33 | 0.26564 | 0.34166 | 0.076019 | 0.038207 | 0.30384 | 0
| 34 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 35 | 0.68756 | 0.51648 | -0.17107 | -0.085982 | 0.60157 | 0
| 36 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 37 | 0.35071 | 0.34192 | -0.0087903 | -0.004418 | 0.3463 | 0
| 38 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 39 | 0.2195 | 0.27641 | 0.05691 | 0.028603 | 0.2481 | 0
| 40 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 41 | 0.49479 | 0.39951 | -0.095278 | -0.047886 | 0.4469 | 0
| 42 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 43 | 0.2178 | 0.25539 | 0.037592 | 0.018894 | 0.23669 | 0
| 44 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 45 | 0.18455 | 0.21867 | 0.034114 | 0.017146 | 0.2017 | 0
| 46 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 47 | 0.41294 | 0.29406 | -0.11888 | -0.059751 | 0.35319 | 0
| 48 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
| 49 | 0.16068 | 0.19636 | 0.035679 | 0.017932 | 0.17861 | 0
| 50 | 0.18458 | 0.21861 | 0.034037 | 0.017107 | 0.20168 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 108.8075 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B03 (hidden)
B03 | Drive row | 38490.0179 | Isc/Iload | 5.5 | 5.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.97 | PF
6 Pulse | 20 |  | 7 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 5 | 6 | 1 | 0.5026 | 5.5026
link choke | 1 | 6 | 7 |  |  | 100 | 0 | Ifund
| 2 | 0.010787 | 0.015489 | 0.0047015 | 0.002363 | 0.01315 | 0
2.5% AC | 3 | 7.7609 | 5.1366 | -2.6243 | -1.319 | 6.4419 | 0
reactor | 4 | 0.018917 | 0.024592 | 0.0056751 | 0.0028523 | 0.021769 | 0
| 5 | 37.2795 | 34.2404 | -3.039 | -1.5274 | 35.7521 | 0
| 6 | 0.0067285 | 0.0045195 | -0.002209 | -0.0011103 | 0.0056183 | 0
| 7 | 10.4074 | 8.4234 | -1.9839 | -0.99713 | 9.4102 | 0
| 8 | 0.019604 | 0.012637 | -0.0069673 | -0.0035017 | 0.016102 | 0
| 9 | 1.5533 | 0.98716 | -0.5661 | -0.28452 | 1.2687 | 0
| 10 | 0.012351 | 0.0078771 | -0.0044741 | -0.0022487 | 0.010102 | 0
| 11 | 6.9056 | 6.5341 | -0.37145 | -0.18669 | 6.7189 | 0
| 12 | 0.004634 | 0.0012659 | -0.0033681 | -0.0016928 | 0.0029412 | 0
| 13 | 3.2688 | 3.1927 | -0.076087 | -0.038241 | 3.2305 | 0
| 14 | 0.013986 | 0.013727 | -0.00025989 | -0.00013062 | 0.013856 | 0
| 15 | 0.77397 | 0.4769 | -0.29708 | -0.14931 | 0.62466 | 0
| 16 | 0.0093355 | 0.011177 | 0.001841 | 0.00092528 | 0.010261 | 0
| 17 | 2.7955 | 2.4617 | -0.33375 | -0.16774 | 2.6278 | 0
| 18 | 0.0032625 | 0.00097249 | -0.00229 | -0.0011509 | 0.0021115 | 0
| 19 | 1.8153 | 1.7533 | -0.061916 | -0.031119 | 1.7841 | 0
| 20 | 0.011519 | 0.012483 | 0.00096337 | 0.00048419 | 0.012003 | 0
| 21 | 0.51233 | 0.3364 | -0.17593 | -0.088422 | 0.42391 | 0
| 22 | 0.013328 | 0.0099334 | -0.0033949 | -0.0017063 | 0.011622 | 0
| 23 | 1.3645 | 1.1709 | -0.19361 | -0.097306 | 1.2672 | 0
| 24 | 0.0058117 | 0.0029855 | -0.0028261 | -0.0014204 | 0.0043913 | 0
| 25 | 1.0203 | 0.89182 | -0.12849 | -0.064576 | 0.95573 | 0
| 26 | 0.012262 | 0.011494 | -0.00076741 | -0.0003857 | 0.011876 | 0
| 27 | 0.40809 | 0.28326 | -0.12483 | -0.062739 | 0.34535 | 0
| 28 | 0.012557 | 0.010538 | -0.002019 | -0.0010147 | 0.011542 | 0
| 29 | 0.75871 | 0.75679 | -0.0019172 | -0.0009636 | 0.75774 | 0
| 30 | 0.0046053 | 0.0036992 | -0.00090615 | -0.00045543 | 0.0041499 | 0
| 31 | 0.56773 | 0.46222 | -0.10551 | -0.053029 | 0.5147 | 0
| 32 | 0.0088971 | 0.011901 | 0.0030043 | 0.00151 | 0.010407 | 0
| 33 | 0.34166 | 0.22742 | -0.11423 | -0.057413 | 0.28424 | 0
| 34 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 35 | 0.51648 | 0.56585 | 0.049367 | 0.024812 | 0.54129 | 0
| 36 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 37 | 0.34192 | 0.32136 | -0.02056 | -0.010334 | 0.33159 | 0
| 38 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 39 | 0.27641 | 0.17818 | -0.098223 | -0.049367 | 0.22704 | 0
| 40 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 41 | 0.39951 | 0.41595 | 0.016433 | 0.008259 | 0.40777 | 0
| 42 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 43 | 0.25539 | 0.24819 | -0.0072008 | -0.0036191 | 0.25177 | 0
| 44 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 45 | 0.21867 | 0.14808 | -0.070582 | -0.035474 | 0.18319 | 0
| 46 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 47 | 0.29406 | 0.27869 | -0.015368 | -0.007724 | 0.28633 | 0
| 48 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
| 49 | 0.19636 | 0.18022 | -0.016136 | -0.0081097 | 0.18825 | 0
| 50 | 0.21861 | 0.14805 | -0.070559 | -0.035463 | 0.18315 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 107.1485 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B04 (hidden)
B04 | Drive row | 38490.0179 | Isc/Iload | 6 | 6.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.965 | PF
6 Pulse | 21 |  | 8 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 6 | 7 | 1 | 0.0025981 | 6.0026
link choke | 1 | 7 | 8 |  |  | 100 | 0 | Ifund
| 2 | 0.015489 | 0.011121 | -0.0043679 | -1.1348e-05 | 0.015477 | 0
3% AC | 3 | 5.1366 | 3.7115 | -1.425 | -0.0037023 | 5.1329 | 0
reactor | 4 | 0.024592 | 0.02231 | -0.0022819 | -5.9287e-06 | 0.024586 | 0
| 5 | 34.2404 | 31.8018 | -2.4386 | -0.0063357 | 34.2341 | 0
| 6 | 0.0045195 | 0.006017 | 0.0014975 | 3.8906e-06 | 0.0045234 | 0
| 7 | 8.4234 | 7.3447 | -1.0787 | -0.0028025 | 8.4206 | 0
| 8 | 0.012637 | 0.010643 | -0.0019933 | -5.1788e-06 | 0.012631 | 0
| 9 | 0.98716 | 0.68104 | -0.30612 | -0.00079533 | 0.98637 | 0
| 10 | 0.0078771 | 0.0066241 | -0.0012529 | -3.2552e-06 | 0.0078738 | 0
| 11 | 6.5341 | 6.0786 | -0.4555 | -0.0011834 | 6.5329 | 0
| 12 | 0.0012659 | 0.00072345 | -0.00054244 | -1.4093e-06 | 0.0012645 | 0
| 13 | 3.1927 | 3.159 | -0.03367 | -8.7476e-05 | 3.1926 | 0
| 14 | 0.013727 | 0.012923 | -0.00080384 | -2.0884e-06 | 0.013724 | 0
| 15 | 0.4769 | 0.32445 | -0.15244 | -0.00039606 | 0.4765 | 0
| 16 | 0.011177 | 0.010798 | -0.00037869 | -9.8388e-07 | 0.011176 | 0
| 17 | 2.4617 | 2.1281 | -0.33364 | -0.00086683 | 2.4609 | 0
| 18 | 0.00097249 | 0.00053825 | -0.00043424 | -1.1282e-06 | 0.00097136 | 0
| 19 | 1.7533 | 1.6441 | -0.10922 | -0.00028376 | 1.7531 | 0
| 20 | 0.012483 | 0.01066 | -0.001823 | -4.7363e-06 | 0.012478 | 0
| 21 | 0.3364 | 0.24976 | -0.086636 | -0.00022509 | 0.33617 | 0
| 22 | 0.0099334 | 0.0087777 | -0.0011557 | -3.0027e-06 | 0.0099304 | 0
| 23 | 1.1709 | 1.045 | -0.12594 | -0.0003272 | 1.1706 | 0
| 24 | 0.0029855 | 0.0023273 | -0.00065823 | -1.7101e-06 | 0.0029838 | 0
| 25 | 0.89182 | 0.77335 | -0.11847 | -0.00030778 | 0.89151 | 0
| 26 | 0.011494 | 0.011502 | 7.9032e-06 | 2.0533e-08 | 0.011494 | 0
| 27 | 0.28326 | 0.20564 | -0.077626 | -0.00020168 | 0.28306 | 0
| 28 | 0.010538 | 0.0092931 | -0.0012446 | -3.2335e-06 | 0.010534 | 0
| 29 | 0.75679 | 0.75576 | -0.0010286 | -2.6724e-06 | 0.75679 | 0
| 30 | 0.0036992 | 0.0019564 | -0.0017428 | -4.5278e-06 | 0.0036946 | 0
| 31 | 0.46222 | 0.42487 | -0.037353 | -9.7046e-05 | 0.46212 | 0
| 32 | 0.011901 | 0.011922 | 2.0283e-05 | 5.2698e-08 | 0.011901 | 0
| 33 | 0.22742 | 0.15382 | -0.073606 | -0.00019123 | 0.22723 | 0
| 34 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 35 | 0.56585 | 0.55172 | -0.014126 | -3.67e-05 | 0.56581 | 0
| 36 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 37 | 0.32136 | 0.32334 | 0.0019796 | 5.1432e-06 | 0.32137 | 0
| 38 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 39 | 0.17818 | 0.12256 | -0.055622 | -0.00014451 | 0.17804 | 0
| 40 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 41 | 0.41595 | 0.37579 | -0.040156 | -0.00010433 | 0.41584 | 0
| 42 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 43 | 0.24819 | 0.22309 | -0.0251 | -6.5212e-05 | 0.24812 | 0
| 44 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 45 | 0.14808 | 0.10867 | -0.039411 | -0.00010239 | 0.14798 | 0
| 46 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 47 | 0.27869 | 0.26697 | -0.011716 | -3.0439e-05 | 0.27866 | 0
| 48 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
| 49 | 0.18022 | 0.15241 | -0.027811 | -7.2255e-05 | 0.18015 | 0
| 50 | 0.14805 | 0.10866 | -0.039397 | -0.00010236 | 0.14795 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 106.4737 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B05 (hidden)
B05 | Drive row | 38490.0179 | Isc/Iload | 8 | 8.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.96 | PF
6 Pulse | 22 |  | 10 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 8 | 10 | 2 | 0.001299 | 8.0026
link choke | 1 | 9 | 10 |  |  | 100 | 0 | Ifund
| 2 | 0.012572 | 0.026363 | 0.013791 | 1.7915e-05 | 0.01259 | 0
5% AC | 3 | 2.8653 | 1.9764 | -0.88883 | -0.0011546 | 2.8641 | 0
reactor | 4 | 0.014672 | 0.0034978 | -0.011174 | -1.4516e-05 | 0.014658 | 0
| 5 | 29.8339 | 26.8294 | -3.0045 | -0.0039029 | 29.83 | 0
| 6 | 0.007333 | 0.0049368 | -0.0023962 | -3.1128e-06 | 0.0073299 | 0
| 7 | 6.8023 | 6.5167 | -0.2856 | -0.000371 | 6.8019 | 0
| 8 | 0.0043474 | 0.0025416 | -0.0018058 | -2.3458e-06 | 0.004345 | 0
| 9 | 0.5061 | 0.31868 | -0.18742 | -0.00024347 | 0.50586 | 0
| 10 | 0.00095446 | 0.0059001 | 0.0049456 | 6.4246e-06 | 0.00096089 | 0
| 11 | 5.6151 | 4.7731 | -0.842 | -0.0010938 | 5.614 | 0
| 12 | 0.0028138 | 0.0033388 | 0.00052503 | 6.8203e-07 | 0.0028144 | 0
| 13 | 3.1114 | 2.9414 | -0.17004 | -0.00022089 | 3.1112 | 0
| 14 | 0.0067573 | 0.0060541 | -0.00070322 | -9.1351e-07 | 0.0067564 | 0
| 15 | 0.24591 | 0.17864 | -0.06727 | -8.7386e-05 | 0.24582 | 0
| 16 | 0.0049258 | 0.0015412 | -0.0033846 | -4.3967e-06 | 0.0049214 | 0
| 17 | 1.8506 | 1.5325 | -0.31808 | -0.0004132 | 1.8502 | 0
| 18 | 0.0034208 | 0.0023022 | -0.0011186 | -1.4531e-06 | 0.0034193 | 0
| 19 | 1.5015 | 1.1979 | -0.30363 | -0.00039443 | 1.5011 | 0
| 20 | 0.0039991 | 0.0042899 | 0.00029086 | 3.7784e-07 | 0.0039994 | 0
| 21 | 0.20144 | 0.14886 | -0.052576 | -6.8298e-05 | 0.20137 | 0
| 22 | 0.0028423 | 0.0017693 | -0.001073 | -1.3938e-06 | 0.0028409 | 0
| 23 | 0.98669 | 0.97152 | -0.015169 | -1.9705e-05 | 0.98667 | 0
| 24 | 0.0031075 | 0.0016642 | -0.0014433 | -1.8749e-06 | 0.0031057 | 0
| 25 | 0.68094 | 0.60411 | -0.076836 | -9.9813e-05 | 0.68084 | 0
| 26 | 0.0063587 | 0.0057283 | -0.00063035 | -8.1884e-07 | 0.0063579 | 0
| 27 | 0.15761 | 0.099377 | -0.058228 | -7.564e-05 | 0.15753 | 0
| 28 | 0.003309 | 0.0008443 | -0.0024647 | -3.2018e-06 | 0.0033058 | 0
| 29 | 0.72479 | 0.61841 | -0.10638 | -0.00013819 | 0.72465 | 0
| 30 | 0.0028718 | 0.0026822 | -0.00018958 | -2.4627e-07 | 0.0028715 | 0
| 31 | 0.43057 | 0.43268 | 0.0021114 | 2.7427e-06 | 0.43057 | 0
| 32 | 0.0059188 | 0.0045875 | -0.0013313 | -1.7294e-06 | 0.005917 | 0
| 33 | 0.11559 | 0.084151 | -0.031438 | -4.0839e-05 | 0.11555 | 0
| 34 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 35 | 0.48796 | 0.39029 | -0.097671 | -0.00012688 | 0.48784 | 0
| 36 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 37 | 0.31458 | 0.26039 | -0.054192 | -7.0398e-05 | 0.31451 | 0
| 38 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 39 | 0.098387 | 0.071958 | -0.026429 | -3.4333e-05 | 0.098353 | 0
| 40 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 41 | 0.3244 | 0.3053 | -0.019102 | -2.4815e-05 | 0.32438 | 0
| 42 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 43 | 0.19779 | 0.1877 | -0.010089 | -1.3105e-05 | 0.19778 | 0
| 44 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 45 | 0.087933 | 0.058262 | -0.029671 | -3.8544e-05 | 0.087894 | 0
| 46 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 47 | 0.26065 | 0.23679 | -0.023852 | -3.0985e-05 | 0.26061 | 0
| 48 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 49 | 0.14568 | 0.14317 | -0.0025146 | -3.2665e-06 | 0.14568 | 0
| 50 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 104.8541 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B06 (hidden)
B06 | Drive row | 38490.0179 | Isc/Iload | 10 | 10.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.955 | PF
6 Pulse | 23 |  | 11 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 10 | 12 | 2 | 0.001299 | 10.0026
link choke | 1 | 10 | 11 |  |  | 100 | 0 | Ifund
| 2 | 0.026363 | 0.0039069 | -0.022456 | -2.9171e-05 | 0.026334 | 0
7% AC | 3 | 1.9764 | 1.513 | -0.46344 | -0.00060202 | 1.9758 | 0
reactor | 4 | 0.0034978 | 0.0033184 | -0.00017938 | -2.3302e-07 | 0.0034975 | 0
| 5 | 26.8294 | 24.5244 | -2.3051 | -0.0029944 | 26.8265 | 0
| 6 | 0.0049368 | 0.0021006 | -0.0028362 | -3.6844e-06 | 0.0049331 | 0
| 7 | 6.5167 | 6.6274 | 0.11072 | 0.00014382 | 6.5168 | 0
| 8 | 0.0025416 | 0.0012217 | -0.0013199 | -1.7146e-06 | 0.0025399 | 0
| 9 | 0.31868 | 0.22627 | -0.092415 | -0.00012005 | 0.31856 | 0
| 10 | 0.0059001 | 0.002841 | -0.0030591 | -3.9738e-06 | 0.0058961 | 0
| 11 | 4.7731 | 4.0377 | -0.73537 | -0.00095528 | 4.7722 | 0
| 12 | 0.0033388 | 0.00070415 | -0.0026346 | -3.4225e-06 | 0.0033354 | 0
| 13 | 2.9414 | 2.6891 | -0.25226 | -0.0003277 | 2.9411 | 0
| 14 | 0.0060541 | 0.00088566 | -0.0051685 | -6.714e-06 | 0.0060474 | 0
| 15 | 0.17864 | 0.15239 | -0.026252 | -3.4102e-05 | 0.1786 | 0
| 16 | 0.0015412 | 0.0017707 | 0.00022949 | 2.9812e-07 | 0.0015415 | 0
| 17 | 1.5325 | 1.4252 | -0.10731 | -0.0001394 | 1.5323 | 0
| 18 | 0.0023022 | 0.00071767 | -0.0015845 | -2.0584e-06 | 0.0023002 | 0
| 19 | 1.1979 | 0.96493 | -0.23294 | -0.0003026 | 1.1976 | 0
| 20 | 0.0042899 | 0.0023631 | -0.0019268 | -2.503e-06 | 0.0042874 | 0
| 21 | 0.14886 | 0.11057 | -0.03829 | -4.974e-05 | 0.14881 | 0
| 22 | 0.0017693 | 0.0023684 | 0.00059908 | 7.7823e-07 | 0.0017701 | 0
| 23 | 0.97152 | 0.91499 | -0.056528 | -7.3432e-05 | 0.97145 | 0
| 24 | 0.0016642 | 0.00050466 | -0.0011595 | -1.5063e-06 | 0.0016627 | 0
| 25 | 0.60411 | 0.59625 | -0.0078562 | -1.0206e-05 | 0.6041 | 0
| 26 | 0.0057283 | 0.0014156 | -0.0043127 | -5.6024e-06 | 0.0057227 | 0
| 27 | 0.099377 | 0.075392 | -0.023985 | -3.1158e-05 | 0.099346 | 0
| 28 | 0.0008443 | 0.0017537 | 0.00090938 | 1.1813e-06 | 0.00084548 | 0
| 29 | 0.61841 | 0.50579 | -0.11262 | -0.0001463 | 0.61826 | 0
| 30 | 0.0026822 | 0.00053985 | -0.0021423 | -2.783e-06 | 0.0026794 | 0
| 31 | 0.43268 | 0.37618 | -0.056505 | -7.3402e-05 | 0.43261 | 0
| 32 | 0.0045875 | 0.00127 | -0.0033175 | -4.3096e-06 | 0.0045832 | 0
| 33 | 0.084151 | 0.067504 | -0.016648 | -2.1626e-05 | 0.08413 | 0
| 34 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 35 | 0.39029 | 0.36343 | -0.026859 | -3.489e-05 | 0.39026 | 0
| 36 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 37 | 0.26039 | 0.23294 | -0.027452 | -3.5662e-05 | 0.26035 | 0
| 38 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 39 | 0.071958 | 0.051367 | -0.020591 | -2.6749e-05 | 0.071931 | 0
| 40 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 41 | 0.3053 | 0.27286 | -0.032442 | -4.2144e-05 | 0.30526 | 0
| 42 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 43 | 0.1877 | 0.18025 | -0.0074551 | -9.6844e-06 | 0.18769 | 0
| 44 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 45 | 0.058262 | 0.044255 | -0.014007 | -1.8195e-05 | 0.058243 | 0
| 46 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 47 | 0.23679 | 0.19038 | -0.046409 | -6.0287e-05 | 0.23673 | 0
| 48 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 49 | 0.14317 | 0.11821 | -0.024956 | -3.2419e-05 | 0.14313 | 0
| 50 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 103.9411 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B07 (hidden)
B07 | Drive row | 38490.0179 | Isc/Iload | 13 | 13.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.95 | PF
6 Pulse | 24 |  | 12 | 1.0026 |  |  |  |  | 0 | Harmonic multiplier
3% DC |  | 12 | 14 | 2 | 0.5013 | 13.0026
link choke | 1 | 11 | 12 |  |  | 100 | 0 | Ifund
| 2 | 0.0039069 | 0.017832 | 0.013925 | 0.0069808 | 0.010888 | 0
10% AC | 3 | 1.513 | 1.248 | -0.265 | -0.13285 | 1.3801 | 0
reactor | 4 | 0.0033184 | 0.01838 | 0.015062 | 0.0075504 | 0.010869 | 0
| 5 | 24.5244 | 22.6661 | -1.8582 | -0.93153 | 23.5928 | 0
| 6 | 0.0021006 | 0.0092816 | 0.0071811 | 0.0035999 | 0.0057004 | 0
| 7 | 6.6274 | 6.8022 | 0.17485 | 0.087654 | 6.715 | 0
| 8 | 0.0012217 | 0.0064595 | 0.0052379 | 0.0026257 | 0.0038474 | 0
| 9 | 0.22627 | 0.17898 | -0.047287 | -0.023705 | 0.20256 | 0
| 10 | 0.002841 | 0.0030933 | 0.00025228 | 0.00012647 | 0.0029675 | 0
| 11 | 4.0377 | 3.4442 | -0.59354 | -0.29754 | 3.7402 | 0
| 12 | 0.00070415 | 0.0032867 | 0.0025825 | 0.0012946 | 0.0019988 | 0
| 13 | 2.6891 | 2.4129 | -0.27623 | -0.13847 | 2.5507 | 0
| 14 | 0.00088566 | 0.0045856 | 0.0037 | 0.0018548 | 0.0027405 | 0
| 15 | 0.15239 | 0.1388 | -0.01359 | -0.0068127 | 0.14557 | 0
| 16 | 0.0017707 | 0.0038905 | 0.0021198 | 0.0010627 | 0.0028334 | 0
| 17 | 1.4252 | 1.4118 | -0.013412 | -0.0067233 | 1.4185 | 0
| 18 | 0.00071767 | 0.0016748 | 0.00095713 | 0.00047981 | 0.0011975 | 0
| 19 | 0.96493 | 0.86231 | -0.10263 | -0.051448 | 0.91349 | 0
| 20 | 0.0023631 | 0.0020372 | -0.00032592 | -0.00016338 | 0.0021998 | 0
| 21 | 0.11057 | 0.08691 | -0.023661 | -0.011861 | 0.098709 | 0
| 22 | 0.0023684 | 0.0022688 | -9.9622e-05 | -4.994e-05 | 0.0023185 | 0
| 23 | 0.91499 | 0.81941 | -0.095579 | -0.047914 | 0.86708 | 0
| 24 | 0.00050466 | 0.0024653 | 0.0019606 | 0.00098285 | 0.0014875 | 0
| 25 | 0.59625 | 0.57911 | -0.01714 | -0.0085921 | 0.58766 | 0
| 26 | 0.0014156 | 0.0023592 | 0.0009436 | 0.00047302 | 0.0018887 | 0
| 27 | 0.075392 | 0.068011 | -0.0073801 | -0.0036997 | 0.071692 | 0
| 28 | 0.0017537 | 0.0012486 | -0.00050504 | -0.00025317 | 0.0015005 | 0
| 29 | 0.50579 | 0.46727 | -0.038517 | -0.019309 | 0.48648 | 0
| 30 | 0.00053985 | 0.0008619 | 0.00032205 | 0.00016144 | 0.00070129 | 0
| 31 | 0.37618 | 0.31679 | -0.05939 | -0.029772 | 0.3464 | 0
| 32 | 0.00127 | 0.0022444 | 0.00097446 | 0.0004885 | 0.0017585 | 0
| 33 | 0.067504 | 0.056413 | -0.01109 | -0.0055595 | 0.061944 | 0
| 34 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 35 | 0.36343 | 0.35167 | -0.011768 | -0.0058995 | 0.35754 | 0
| 36 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 37 | 0.23294 | 0.23495 | 0.0020158 | 0.0010105 | 0.23395 | 0
| 38 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 39 | 0.051367 | 0.04285 | -0.0085165 | -0.0042693 | 0.047097 | 0
| 40 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 41 | 0.27286 | 0.23528 | -0.037574 | -0.018836 | 0.25402 | 0
| 42 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 43 | 0.18025 | 0.14969 | -0.030554 | -0.015317 | 0.16493 | 0
| 44 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 45 | 0.044255 | 0.039512 | -0.0047432 | -0.0023778 | 0.041877 | 0
| 46 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 47 | 0.19038 | 0.18456 | -0.005824 | -0.0029196 | 0.18747 | 0
| 48 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
| 49 | 0.11821 | 0.11325 | -0.0049632 | -0.0024881 | 0.11572 | 0
| 50 | 0.044253 | 0.03951 | -0.0047433 | -0.0023778 | 0.041875 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 103.0963 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## B08 (hidden)
B08 | Drive row | 38490.0179 | Isc/Iload | 3 | 3.0026 | %Z | 0 | A | 0 | PU Load |  |  | 0.995 | PF | kW/kVA
6 Pulse | 25 |  | 5 | 0.0025981 |  |  |  |  | 0.1475 | Harmonic multiplier
3% DC |  | 3 | 4 | 1 | 0.0025981 | 3.0026 | [6 empty] | -0.099875 | QF | kVAR/kVA
link choke | 1 | 4 | 5 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.2862 | 0.2862 | 0 | 0 | 0.2862 | 0 |  | 0 | actual hp
7% THDi | 3 | 0.039331 | 0.039331 | 0 | 0 | 0.039331 | 0
filter | 4 | 0.25832 | 0.25832 | 0 | 0 | 0.25832 | 0 |  | -35 | Ifilter at no load, 100hp
| 5 | 4.5719 | 4.5719 | 0 | 0 | 4.5719 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.017666 | 0.017666 | 0 | 0 | 0.017666 | 0
| 7 | 3.2679 | 3.2679 | 0 | 0 | 3.2679 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.017088 | 0.017088 | 0 | 0 | 0.017088 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.0083557 | 0.0083557 | 0 | 0 | 0.0083557 | 0 |  | 0 | Ireact at xpu
| 10 | 0.0047045 | 0.0047045 | 0 | 0 | 0.0047045 | 0
| 11 | 3.0368 | 3.0368 | 0 | 0 | 3.0368 | 0 |  | 0 | Ireal at 1pu
| 12 | 0.0029416 | 0.0029416 | 0 | 0 | 0.0029416 | 0 |  | 0 | Ireal at xpu
| 13 | 1.9571 | 1.9571 | 0 | 0 | 1.9571 | 0
| 14 | 0.010432 | 0.010432 | 0 | 0 | 0.010432 | 0 |  | 0 | Ifund at 1pu
| 15 | 0.0019438 | 0.0019438 | 0 | 0 | 0.0019438 | 0 |  | 0 | Ifund at xpu
| 16 | 0.00873 | 0.00873 | 0 | 0 | 0.00873 | 0
| 17 | 0.97557 | 0.97557 | 0 | 0 | 0.97557 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0026049 | 0.0026049 | 0 | 0 | 0.0026049 | 0
| 19 | 0.91669 | 0.91669 | 0 | 0 | 0.91669 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0034359 | 0.0034359 | 0 | 0 | 0.0034359 | 0
| 21 | 0.0015448 | 0.0015448 | 0 | 0 | 0.0015448 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0052235 | 0.0052235 | 0 | 0 | 0.0052235 | 0
| 23 | 0.54728 | 0.54728 | 0 | 0 | 0.54728 | 0
| 24 | 0.00073681 | 0.00073681 | 0 | 0 | 0.00073681 | 0
| 25 | 0.4394 | 0.4394 | 0 | 0 | 0.4394 | 0
| 26 | 0.0037751 | 0.0037751 | 0 | 0 | 0.0037751 | 0
| 27 | 0.0014496 | 0.0014496 | 0 | 0 | 0.0014496 | 0
| 28 | 0.002311 | 0.002311 | 0 | 0 | 0.002311 | 0
| 29 | 0.39633 | 0.39633 | 0 | 0 | 0.39633 | 0
| 30 | 0.0011457 | 0.0011457 | 0 | 0 | 0.0011457 | 0
| 31 | 0.32608 | 0.32608 | 0 | 0 | 0.32608 | 0
| 32 | 0.0038606 | 0.0038606 | 0 | 0 | 0.0038606 | 0
| 33 | 0.00034023 | 0.00034023 | 0 | 0 | 0.00034023 | 0
| 34 | 0.0038157 | 0.0038157 | 0 | 0 | 0.0038157 | 0
| 35 | 0.24452 | 0.24452 | 0 | 0 | 0.24452 | 0
| 36 | 0.0008725 | 0.0008725 | 0 | 0 | 0.0008725 | 0
| 37 | 0.23543 | 0.23543 | 0 | 0 | 0.23543 | 0
| 38 | 0.0016183 | 0.0016183 | 0 | 0 | 0.0016183 | 0
| 39 | 0.00091856 | 0.00091856 | 0 | 0 | 0.00091856 | 0
| 40 | 0.0021859 | 0.0021859 | 0 | 0 | 0.0021859 | 0
| 41 | 0.17547 | 0.17547 | 0 | 0 | 0.17547 | 0
| 42 | 0.00033318 | 0.00033318 | 0 | 0 | 0.00033318 | 0
| 43 | 0.15609 | 0.15609 | 0 | 0 | 0.15609 | 0
| 44 | 0.0025667 | 0.0025667 | 0 | 0 | 0.0025667 | 0
| 45 | 0.00048875 | 0.00048875 | 0 | 0 | 0.00048875 | 0
| 46 | 0.0019607 | 0.0019607 | 0 | 0 | 0.0019607 | 0
| 47 | 0.14695 | 0.14695 | 0 | 0 | 0.14695 | 0
| 48 | 0.00069771 | 0.00069771 | 0 | 0 | 0.00069771 | 0
| 49 | 0.12856 | 0.12856 | 0 | 0 | 0.12856 | 0
| 50 | 0.0019605 | 0.0019605 | 0 | 0 | 0.0019605 | 0
[5 empty] | thd | 6.8951 | 0 | Iharm
[5 empty] | total | 100.2374 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.32933 | 0.31535 | 0.30142 | 0.28744 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862
3 |  |  | 0.04526 | 0.043339 | 0.041423 | 0.039502 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331
4 |  |  | 0.29726 | 0.28464 | 0.27206 | 0.25945 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832
5 |  |  | 5.261 | 5.0377 | 4.8151 | 4.5918 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719
6 |  |  | 0.020329 | 0.019466 | 0.018605 | 0.017743 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666
7 |  |  | 3.7605 | 3.6009 | 3.4418 | 3.2822 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679
8 |  |  | 0.019663 | 0.018829 | 0.017997 | 0.017162 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088
9 |  |  | 0.0096151 | 0.009207 | 0.0088001 | 0.008392 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557
10 |  |  | 0.0054136 | 0.0051838 | 0.0049547 | 0.004725 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045
11 |  |  | 3.4945 | 3.3462 | 3.1983 | 3.05 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368
12 |  |  | 0.0033849 | 0.0032412 | 0.003098 | 0.0029543 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416
13 |  |  | 2.2521 | 2.1565 | 2.0612 | 1.9656 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571
14 |  |  | 0.012004 | 0.011495 | 0.010987 | 0.010477 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432
15 |  |  | 0.0022368 | 0.0021419 | 0.0020472 | 0.0019523 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438
16 |  |  | 0.010046 | 0.0096194 | 0.0091943 | 0.0087679 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873
17 |  |  | 1.1226 | 1.075 | 1.0275 | 0.97981 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557
18 |  |  | 0.0029975 | 0.0028703 | 0.0027435 | 0.0026162 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049
19 |  |  | 1.0549 | 1.0101 | 0.96545 | 0.92068 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669
20 |  |  | 0.0039537 | 0.0037859 | 0.0036186 | 0.0034508 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359
21 |  |  | 0.0017776 | 0.0017022 | 0.001627 | 0.0015515 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448
22 |  |  | 0.0060108 | 0.0057557 | 0.0055013 | 0.0052462 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235
23 |  |  | 0.62977 | 0.60304 | 0.57639 | 0.54966 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728
24 |  |  | 0.00084787 | 0.00081188 | 0.000776 | 0.00074001 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681
25 |  |  | 0.50563 | 0.48417 | 0.46277 | 0.44131 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394
26 |  |  | 0.0043441 | 0.0041597 | 0.0039759 | 0.0037915 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751
27 |  |  | 0.0016681 | 0.0015973 | 0.0015267 | 0.0014559 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496
28 |  |  | 0.0026594 | 0.0025465 | 0.002434 | 0.0023211 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311
29 |  |  | 0.45607 | 0.43671 | 0.41741 | 0.39805 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633
30 |  |  | 0.0013184 | 0.0012624 | 0.0012066 | 0.0011507 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457
31 |  |  | 0.37522 | 0.3593 | 0.34342 | 0.32749 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608
32 |  |  | 0.0044425 | 0.0042539 | 0.0040659 | 0.0038774 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606
33 |  |  | 0.00039151 | 0.0003749 | 0.00035833 | 0.00034171 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023
34 |  |  | 0.0043909 | 0.0042045 | 0.0040187 | 0.0038323 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157
35 |  |  | 0.28137 | 0.26943 | 0.25752 | 0.24558 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452
36 |  |  | 0.001004 | 0.0009614 | 0.00091891 | 0.0008763 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725
37 |  |  | 0.27092 | 0.25942 | 0.24796 | 0.23646 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543
38 |  |  | 0.0018623 | 0.0017832 | 0.0017044 | 0.0016254 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183
39 |  |  | 0.001057 | 0.0010121 | 0.00096741 | 0.00092255 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856
40 |  |  | 0.0025154 | 0.0024086 | 0.0023021 | 0.0021954 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859
41 |  |  | 0.20192 | 0.19335 | 0.1848 | 0.17623 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547
42 |  |  | 0.0003834 | 0.00036713 | 0.0003509 | 0.00033463 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318
43 |  |  | 0.17961 | 0.17199 | 0.16439 | 0.15677 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609
44 |  |  | 0.0029536 | 0.0028282 | 0.0027032 | 0.0025779 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667
45 |  |  | 0.00056241 | 0.00053854 | 0.00051474 | 0.00049087 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875
46 |  |  | 0.0022562 | 0.0021605 | 0.002065 | 0.0019692 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607
47 |  |  | 0.1691 | 0.16192 | 0.15476 | 0.14759 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695
48 |  |  | 0.00080287 | 0.00076879 | 0.00073482 | 0.00070074 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771
49 |  |  | 0.14794 | 0.14166 | 0.1354 | 0.12912 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856
50 |  |  | 0.0022559 | 0.0021602 | 0.0020647 | 0.001969 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605
| Ithd |  | 7.9343 | 7.5976 | 7.2618 | 6.9251 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951

## B09 (hidden)
B09 | Drive row | 38490.0179 | Isc/Iload | 3 | 3.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.999 | PF | kW/kVA
6 Pulse | 26 |  | 5 | 0.0025981 |  |  |  |  | 1.1251 | Harmonic multiplier
3% DC |  | 3 | 4 | 1 | 0.0025981 | 3.0026 | [6 empty] | 0.04471 | QF | kVAR/kVA
link choke | 1 | 4 | 5 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.20034 | 0.20034 | 0 | 0 | 0.20034 | 0 |  | 0 | actual hp
5% THDi | 3 | 0.027532 | 0.027532 | 0 | 0 | 0.027532 | 0
filter | 4 | 0.18083 | 0.18083 | 0 | 0 | 0.18083 | 0 |  | -40 | Ifilter at no load, 100hp
| 5 | 3.2003 | 3.2003 | 0 | 0 | 3.2003 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.012366 | 0.012366 | 0 | 0 | 0.012366 | 0
| 7 | 2.2876 | 2.2876 | 0 | 0 | 2.2876 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.011961 | 0.011961 | 0 | 0 | 0.011961 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.005849 | 0.005849 | 0 | 0 | 0.005849 | 0 |  | 0 | Ireact at xpu
| 10 | 0.0032932 | 0.0032932 | 0 | 0 | 0.0032932 | 0
| 11 | 2.1258 | 2.1258 | 0 | 0 | 2.1258 | 0 |  | 0 | Ireal at 1pu
| 12 | 0.0020591 | 0.0020591 | 0 | 0 | 0.0020591 | 0 |  | 0 | Ireal at xpu
| 13 | 1.37 | 1.37 | 0 | 0 | 1.37 | 0
| 14 | 0.0073022 | 0.0073022 | 0 | 0 | 0.0073022 | 0 |  | 0 | Ifund at 1pu
| 15 | 0.0013607 | 0.0013607 | 0 | 0 | 0.0013607 | 0 |  | 0 | Ifund at xpu
| 16 | 0.006111 | 0.006111 | 0 | 0 | 0.006111 | 0
| 17 | 0.6829 | 0.6829 | 0 | 0 | 0.6829 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0018234 | 0.0018234 | 0 | 0 | 0.0018234 | 0
| 19 | 0.64169 | 0.64169 | 0 | 0 | 0.64169 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0024051 | 0.0024051 | 0 | 0 | 0.0024051 | 0
| 21 | 0.0010814 | 0.0010814 | 0 | 0 | 0.0010814 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0036564 | 0.0036564 | 0 | 0 | 0.0036564 | 0
| 23 | 0.3831 | 0.3831 | 0 | 0 | 0.3831 | 0
| 24 | 0.00051577 | 0.00051577 | 0 | 0 | 0.00051577 | 0
| 25 | 0.30758 | 0.30758 | 0 | 0 | 0.30758 | 0
| 26 | 0.0026426 | 0.0026426 | 0 | 0 | 0.0026426 | 0
| 27 | 0.0010147 | 0.0010147 | 0 | 0 | 0.0010147 | 0
| 28 | 0.0016177 | 0.0016177 | 0 | 0 | 0.0016177 | 0
| 29 | 0.27743 | 0.27743 | 0 | 0 | 0.27743 | 0
| 30 | 0.00080198 | 0.00080198 | 0 | 0 | 0.00080198 | 0
| 31 | 0.22825 | 0.22825 | 0 | 0 | 0.22825 | 0
| 32 | 0.0027024 | 0.0027024 | 0 | 0 | 0.0027024 | 0
| 33 | 0.00023816 | 0.00023816 | 0 | 0 | 0.00023816 | 0
| 34 | 0.002671 | 0.002671 | 0 | 0 | 0.002671 | 0
| 35 | 0.17116 | 0.17116 | 0 | 0 | 0.17116 | 0
| 36 | 0.00061075 | 0.00061075 | 0 | 0 | 0.00061075 | 0
| 37 | 0.1648 | 0.1648 | 0 | 0 | 0.1648 | 0
| 38 | 0.0011328 | 0.0011328 | 0 | 0 | 0.0011328 | 0
| 39 | 0.00064299 | 0.00064299 | 0 | 0 | 0.00064299 | 0
| 40 | 0.0015301 | 0.0015301 | 0 | 0 | 0.0015301 | 0
| 41 | 0.12283 | 0.12283 | 0 | 0 | 0.12283 | 0
| 42 | 0.00023323 | 0.00023323 | 0 | 0 | 0.00023323 | 0
| 43 | 0.10926 | 0.10926 | 0 | 0 | 0.10926 | 0
| 44 | 0.0017967 | 0.0017967 | 0 | 0 | 0.0017967 | 0
| 45 | 0.00034212 | 0.00034212 | 0 | 0 | 0.00034212 | 0
| 46 | 0.0013725 | 0.0013725 | 0 | 0 | 0.0013725 | 0
| 47 | 0.10286 | 0.10286 | 0 | 0 | 0.10286 | 0
| 48 | 0.0004884 | 0.0004884 | 0 | 0 | 0.0004884 | 0
| 49 | 0.089995 | 0.089995 | 0 | 0 | 0.089995 | 0
| 50 | 0.0013723 | 0.0013723 | 0 | 0 | 0.0013723 | 0
[5 empty] | thd | 4.8266 | 0 | Iharm
[5 empty] | total | 100.1164 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.20697 | 0.20519 | 0.20336 | 0.20158 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034
3 |  |  | 0.028444 | 0.028199 | 0.027948 | 0.027703 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532
4 |  |  | 0.18682 | 0.18521 | 0.18356 | 0.18195 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083
5 |  |  | 3.3064 | 3.2779 | 3.2487 | 3.2202 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003
6 |  |  | 0.012776 | 0.012666 | 0.012553 | 0.012443 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366
7 |  |  | 2.3633 | 2.343 | 2.3221 | 2.3018 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876
8 |  |  | 0.012358 | 0.012251 | 0.012142 | 0.012036 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961
9 |  |  | 0.0060427 | 0.0059906 | 0.0059374 | 0.0058853 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849
10 |  |  | 0.0034023 | 0.0033729 | 0.0033429 | 0.0033136 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932
11 |  |  | 2.1962 | 2.1773 | 2.1579 | 2.139 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258
12 |  |  | 0.0021273 | 0.002109 | 0.0020902 | 0.0020719 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591
13 |  |  | 1.4153 | 1.4031 | 1.3907 | 1.3785 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37
14 |  |  | 0.0075441 | 0.0074791 | 0.0074125 | 0.0073475 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022
15 |  |  | 0.0014058 | 0.0013936 | 0.0013812 | 0.0013691 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607
16 |  |  | 0.0063134 | 0.006259 | 0.0062033 | 0.0061489 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111
17 |  |  | 0.70552 | 0.69944 | 0.69322 | 0.68714 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829
18 |  |  | 0.0018838 | 0.0018676 | 0.001851 | 0.0018348 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234
19 |  |  | 0.66294 | 0.65723 | 0.65138 | 0.64567 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169
20 |  |  | 0.0024848 | 0.0024634 | 0.0024415 | 0.00242 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051
21 |  |  | 0.0011172 | 0.0011075 | 0.0010977 | 0.0010881 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814
22 |  |  | 0.0037776 | 0.003745 | 0.0037117 | 0.0036791 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564
23 |  |  | 0.39579 | 0.39238 | 0.38889 | 0.38548 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831
24 |  |  | 0.00053285 | 0.00052826 | 0.00052356 | 0.00051897 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577
25 |  |  | 0.31777 | 0.31503 | 0.31223 | 0.30949 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758
26 |  |  | 0.0027301 | 0.0027066 | 0.0026825 | 0.002659 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426
27 |  |  | 0.0010483 | 0.0010393 | 0.00103 | 0.001021 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147
28 |  |  | 0.0016713 | 0.0016569 | 0.0016422 | 0.0016278 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177
29 |  |  | 0.28662 | 0.28415 | 0.28163 | 0.27916 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743
30 |  |  | 0.00082855 | 0.00082141 | 0.0008141 | 0.00080696 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198
31 |  |  | 0.23581 | 0.23378 | 0.2317 | 0.22967 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825
32 |  |  | 0.0027919 | 0.0027679 | 0.0027432 | 0.0027192 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024
33 |  |  | 0.00024605 | 0.00024393 | 0.00024176 | 0.00023964 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816
34 |  |  | 0.0027595 | 0.0027357 | 0.0027114 | 0.0026876 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671
35 |  |  | 0.17683 | 0.17531 | 0.17375 | 0.17222 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116
36 |  |  | 0.00063098 | 0.00062555 | 0.00061998 | 0.00061454 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075
37 |  |  | 0.17026 | 0.1688 | 0.16729 | 0.16583 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648
38 |  |  | 0.0011704 | 0.0011603 | 0.00115 | 0.0011399 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328
39 |  |  | 0.00066429 | 0.00065857 | 0.00065271 | 0.00064698 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299
40 |  |  | 0.0015808 | 0.0015672 | 0.0015532 | 0.0015396 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301
41 |  |  | 0.1269 | 0.12581 | 0.12469 | 0.12359 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283
42 |  |  | 0.00024095 | 0.00023888 | 0.00023675 | 0.00023468 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323
43 |  |  | 0.11288 | 0.11191 | 0.11091 | 0.10994 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926
44 |  |  | 0.0018562 | 0.0018402 | 0.0018239 | 0.0018079 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967
45 |  |  | 0.00035346 | 0.00035041 | 0.00034729 | 0.00034425 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212
46 |  |  | 0.001418 | 0.0014057 | 0.0013932 | 0.001381 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725
47 |  |  | 0.10627 | 0.10536 | 0.10442 | 0.1035 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286
48 |  |  | 0.00050457 | 0.00050023 | 0.00049578 | 0.00049143 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884
49 |  |  | 0.092976 | 0.092175 | 0.091355 | 0.090554 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995
50 |  |  | 0.0014178 | 0.0014056 | 0.0013931 | 0.0013808 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723
| Ithd |  | 4.9864 | 4.9435 | 4.8995 | 4.8565 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266

## C01 (hidden)
C01 | Drive row | 38490.0179 | Isc/Iload | 5 | 5.0026 | %Z | 0 | A | 0 | PU Load |  |  | 0.965 | PF
6 Pulse | 30 |  | 7 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 5 | 6 | 1 | 0.0025981 | 5.0026
link choke | 1 | 6 | 7 |  |  | 100 | 0 | Ifund
| 2 | 0.010787 | 0.015489 | 0.0047015 | 1.2215e-05 | 0.0108 | 0
no line | 3 | 7.7609 | 5.1366 | -2.6243 | -0.0068181 | 7.754 | 0
reactor | 4 | 0.018917 | 0.024592 | 0.0056751 | 1.4744e-05 | 0.018932 | 0
| 5 | 37.2795 | 34.2404 | -3.039 | -0.0078956 | 37.2716 | 0
| 6 | 0.0067285 | 0.0045195 | -0.002209 | -5.7392e-06 | 0.0067228 | 0
| 7 | 10.4074 | 8.4234 | -1.9839 | -0.0051544 | 10.4022 | 0
| 8 | 0.019604 | 0.012637 | -0.0069673 | -1.8102e-05 | 0.019586 | 0
| 9 | 1.5533 | 0.98716 | -0.5661 | -0.0014708 | 1.5518 | 0
| 10 | 0.012351 | 0.0078771 | -0.0044741 | -1.1624e-05 | 0.01234 | 0
| 11 | 6.9056 | 6.5341 | -0.37145 | -0.00096505 | 6.9046 | 0
| 12 | 0.004634 | 0.0012659 | -0.0033681 | -8.7507e-06 | 0.0046253 | 0
| 13 | 3.2688 | 3.1927 | -0.076087 | -0.00019768 | 3.2686 | 0
| 14 | 0.013986 | 0.013727 | -0.00025989 | -6.7522e-07 | 0.013986 | 0
| 15 | 0.77397 | 0.4769 | -0.29708 | -0.00077182 | 0.7732 | 0
| 16 | 0.0093355 | 0.011177 | 0.001841 | 4.783e-06 | 0.0093403 | 0
| 17 | 2.7955 | 2.4617 | -0.33375 | -0.00086711 | 2.7946 | 0
| 18 | 0.0032625 | 0.00097249 | -0.00229 | -5.9495e-06 | 0.0032565 | 0
| 19 | 1.8153 | 1.7533 | -0.061916 | -0.00016086 | 1.8151 | 0
| 20 | 0.011519 | 0.012483 | 0.00096337 | 2.5029e-06 | 0.011522 | 0
| 21 | 0.51233 | 0.3364 | -0.17593 | -0.00045708 | 0.51187 | 0
| 22 | 0.013328 | 0.0099334 | -0.0033949 | -8.8201e-06 | 0.013319 | 0
| 23 | 1.3645 | 1.1709 | -0.19361 | -0.000503 | 1.364 | 0
| 24 | 0.0058117 | 0.0029855 | -0.0028261 | -7.3425e-06 | 0.0058043 | 0
| 25 | 1.0203 | 0.89182 | -0.12849 | -0.00033381 | 1.02 | 0
| 26 | 0.012262 | 0.011494 | -0.00076741 | -1.9938e-06 | 0.01226 | 0
| 27 | 0.40809 | 0.28326 | -0.12483 | -0.00032432 | 0.40777 | 0
| 28 | 0.012557 | 0.010538 | -0.002019 | -5.2455e-06 | 0.012551 | 0
| 29 | 0.75871 | 0.75679 | -0.0019172 | -4.9811e-06 | 0.7587 | 0
| 30 | 0.0046053 | 0.0036992 | -0.00090615 | -2.3542e-06 | 0.004603 | 0
| 31 | 0.56773 | 0.46222 | -0.10551 | -0.00027412 | 0.56745 | 0
| 32 | 0.0088971 | 0.011901 | 0.0030043 | 7.8054e-06 | 0.0089049 | 0
| 33 | 0.34166 | 0.22742 | -0.11423 | -0.00029679 | 0.34136 | 0
| 34 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 35 | 0.51648 | 0.56585 | 0.049367 | 0.00012826 | 0.51661 | 0
| 36 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 37 | 0.34192 | 0.32136 | -0.02056 | -5.3418e-05 | 0.34187 | 0
| 38 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 39 | 0.27641 | 0.17818 | -0.098223 | -0.00025519 | 0.27615 | 0
| 40 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 41 | 0.39951 | 0.41595 | 0.016433 | 4.2693e-05 | 0.39956 | 0
| 42 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 43 | 0.25539 | 0.24819 | -0.0072008 | -1.8708e-05 | 0.25537 | 0
| 44 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 45 | 0.21867 | 0.14808 | -0.070582 | -0.00018338 | 0.21848 | 0
| 46 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 47 | 0.29406 | 0.27869 | -0.015368 | -3.9928e-05 | 0.29402 | 0
| 48 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
| 49 | 0.19636 | 0.18022 | -0.016136 | -4.1922e-05 | 0.19632 | 0
| 50 | 0.21861 | 0.14805 | -0.070559 | -0.00018332 | 0.21843 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 107.8684 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C02 (hidden)
C02 | Drive row | 38490.0179 | Isc/Iload | 6.5 | 6.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.965 | PF
6 Pulse | 31 |  | 8 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 6 | 7 | 1 | 0.5026 | 6.5026
link choke | 1 | 7 | 8 |  |  | 100 | 0 | Ifund
| 2 | 0.015489 | 0.011121 | -0.0043679 | -0.0021953 | 0.013294 | 0
1.5% AC | 3 | 5.1366 | 3.7115 | -1.425 | -0.71621 | 4.4203 | 0
reactor | 4 | 0.024592 | 0.02231 | -0.0022819 | -0.0011469 | 0.023445 | 0
| 5 | 34.2404 | 31.8018 | -2.4386 | -1.2256 | 33.0148 | 0
| 6 | 0.0045195 | 0.006017 | 0.0014975 | 0.00075263 | 0.0052721 | 0
| 7 | 8.4234 | 7.3447 | -1.0787 | -0.54214 | 7.8813 | 0
| 8 | 0.012637 | 0.010643 | -0.0019933 | -0.0010018 | 0.011635 | 0
| 9 | 0.98716 | 0.68104 | -0.30612 | -0.15386 | 0.83331 | 0
| 10 | 0.0078771 | 0.0066241 | -0.0012529 | -0.00062972 | 0.0072474 | 0
| 11 | 6.5341 | 6.0786 | -0.4555 | -0.22894 | 6.3052 | 0
| 12 | 0.0012659 | 0.00072345 | -0.00054244 | -0.00027263 | 0.00099326 | 0
| 13 | 3.1927 | 3.159 | -0.03367 | -0.016922 | 3.1758 | 0
| 14 | 0.013727 | 0.012923 | -0.00080384 | -0.00040401 | 0.013323 | 0
| 15 | 0.4769 | 0.32445 | -0.15244 | -0.076618 | 0.40028 | 0
| 16 | 0.011177 | 0.010798 | -0.00037869 | -0.00019033 | 0.010986 | 0
| 17 | 2.4617 | 2.1281 | -0.33364 | -0.16769 | 2.2941 | 0
| 18 | 0.00097249 | 0.00053825 | -0.00043424 | -0.00021825 | 0.00075424 | 0
| 19 | 1.7533 | 1.6441 | -0.10922 | -0.054893 | 1.6984 | 0
| 20 | 0.012483 | 0.01066 | -0.001823 | -0.00091623 | 0.011566 | 0
| 21 | 0.3364 | 0.24976 | -0.086636 | -0.043543 | 0.29286 | 0
| 22 | 0.0099334 | 0.0087777 | -0.0011557 | -0.00058087 | 0.0093526 | 0
| 23 | 1.1709 | 1.045 | -0.12594 | -0.063297 | 1.1076 | 0
| 24 | 0.0029855 | 0.0023273 | -0.00065823 | -0.00033082 | 0.0026547 | 0
| 25 | 0.89182 | 0.77335 | -0.11847 | -0.059541 | 0.83228 | 0
| 26 | 0.011494 | 0.011502 | 7.9032e-06 | 3.9721e-06 | 0.011498 | 0
| 27 | 0.28326 | 0.20564 | -0.077626 | -0.039015 | 0.24425 | 0
| 28 | 0.010538 | 0.0092931 | -0.0012446 | -0.00062552 | 0.0099121 | 0
| 29 | 0.75679 | 0.75576 | -0.0010286 | -0.00051697 | 0.75627 | 0
| 30 | 0.0036992 | 0.0019564 | -0.0017428 | -0.00087591 | 0.0028233 | 0
| 31 | 0.46222 | 0.42487 | -0.037353 | -0.018773 | 0.44345 | 0
| 32 | 0.011901 | 0.011922 | 2.0283e-05 | 1.0194e-05 | 0.011912 | 0
| 33 | 0.22742 | 0.15382 | -0.073606 | -0.036994 | 0.19043 | 0
| 34 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 35 | 0.56585 | 0.55172 | -0.014126 | -0.0070996 | 0.55875 | 0
| 36 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 37 | 0.32136 | 0.32334 | 0.0019796 | 0.00099495 | 0.32236 | 0
| 38 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 39 | 0.17818 | 0.12256 | -0.055622 | -0.027956 | 0.15023 | 0
| 40 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 41 | 0.41595 | 0.37579 | -0.040156 | -0.020182 | 0.39576 | 0
| 42 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 43 | 0.24819 | 0.22309 | -0.0251 | -0.012615 | 0.23557 | 0
| 44 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 45 | 0.14808 | 0.10867 | -0.039411 | -0.019808 | 0.12828 | 0
| 46 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 47 | 0.27869 | 0.26697 | -0.011716 | -0.0058884 | 0.2728 | 0
| 48 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
| 49 | 0.18022 | 0.15241 | -0.027811 | -0.013978 | 0.16625 | 0
| 50 | 0.14805 | 0.10866 | -0.039397 | -0.019801 | 0.12825 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 105.9918 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C03 (hidden)
C03 | Drive row | 38490.0179 | Isc/Iload | 7.5 | 7.5026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.96 | PF
6 Pulse | 32 |  | 9 | 0.5026 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 7 | 8 | 1 | 0.5026 | 7.5026
link choke | 1 | 8 | 9 |  |  | 100 | 0 | Ifund
| 2 | 0.011121 | 0.012572 | 0.001451 | 0.00072926 | 0.01185 | 0
2.5% AC | 3 | 3.7115 | 2.8653 | -0.84628 | -0.42534 | 3.2862 | 0
reactor | 4 | 0.02231 | 0.014672 | -0.0076378 | -0.0038387 | 0.018471 | 0
| 5 | 31.8018 | 29.8339 | -1.9679 | -0.98907 | 30.8128 | 0
| 6 | 0.006017 | 0.007333 | 0.0013161 | 0.00066145 | 0.0066784 | 0
| 7 | 7.3447 | 6.8023 | -0.54248 | -0.27265 | 7.0721 | 0
| 8 | 0.010643 | 0.0043474 | -0.006296 | -0.0031643 | 0.007479 | 0
| 9 | 0.68104 | 0.5061 | -0.17494 | -0.087923 | 0.59312 | 0
| 10 | 0.0066241 | 0.00095446 | -0.0056697 | -0.0028496 | 0.0037746 | 0
| 11 | 6.0786 | 5.6151 | -0.46349 | -0.23295 | 5.8457 | 0
| 12 | 0.00072345 | 0.0028138 | 0.0020903 | 0.0010506 | 0.001774 | 0
| 13 | 3.159 | 3.1114 | -0.047592 | -0.02392 | 3.1351 | 0
| 14 | 0.012923 | 0.0067573 | -0.0061654 | -0.0030987 | 0.009824 | 0
| 15 | 0.32445 | 0.24591 | -0.078547 | -0.039478 | 0.28498 | 0
| 16 | 0.010798 | 0.0049258 | -0.005872 | -0.0029512 | 0.0078466 | 0
| 17 | 2.1281 | 1.8506 | -0.27754 | -0.13949 | 1.9886 | 0
| 18 | 0.00053825 | 0.0034208 | 0.0028825 | 0.0014488 | 0.001987 | 0
| 19 | 1.6441 | 1.5015 | -0.14261 | -0.071676 | 1.5724 | 0
| 20 | 0.01066 | 0.0039991 | -0.0066605 | -0.0033476 | 0.007312 | 0
| 21 | 0.24976 | 0.20144 | -0.048326 | -0.024289 | 0.22547 | 0
| 22 | 0.0087777 | 0.0028423 | -0.0059354 | -0.0029831 | 0.0057946 | 0
| 23 | 1.045 | 0.98669 | -0.058274 | -0.029289 | 1.0157 | 0
| 24 | 0.0023273 | 0.0031075 | 0.00078023 | 0.00039214 | 0.0027194 | 0
| 25 | 0.77335 | 0.68094 | -0.09241 | -0.046445 | 0.72691 | 0
| 26 | 0.011502 | 0.0063587 | -0.0051435 | -0.0025851 | 0.0089171 | 0
| 27 | 0.20564 | 0.15761 | -0.048031 | -0.02414 | 0.1815 | 0
| 28 | 0.0092931 | 0.003309 | -0.0059841 | -0.0030076 | 0.0062855 | 0
| 29 | 0.75576 | 0.72479 | -0.030975 | -0.015568 | 0.74019 | 0
| 30 | 0.0019564 | 0.0028718 | 0.00091535 | 0.00046005 | 0.0024165 | 0
| 31 | 0.42487 | 0.43057 | 0.005703 | 0.0028663 | 0.42773 | 0
| 32 | 0.011922 | 0.0059188 | -0.0060029 | -0.003017 | 0.0089046 | 0
| 33 | 0.15382 | 0.11559 | -0.038227 | -0.019213 | 0.1346 | 0
| 34 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 35 | 0.55172 | 0.48796 | -0.063757 | -0.032044 | 0.51968 | 0
| 36 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 37 | 0.32334 | 0.31458 | -0.0087615 | -0.0044035 | 0.31894 | 0
| 38 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 39 | 0.12256 | 0.098387 | -0.024175 | -0.01215 | 0.11041 | 0
| 40 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 41 | 0.37579 | 0.3244 | -0.051389 | -0.025828 | 0.34996 | 0
| 42 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 43 | 0.22309 | 0.19779 | -0.025298 | -0.012715 | 0.21037 | 0
| 44 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 45 | 0.10867 | 0.087933 | -0.02074 | -0.010424 | 0.098249 | 0
| 46 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 47 | 0.26697 | 0.26065 | -0.0063268 | -0.0031798 | 0.26379 | 0
| 48 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
| 49 | 0.15241 | 0.14568 | -0.0067312 | -0.0033831 | 0.14903 | 0
| 50 | 0.10866 | 0.087922 | -0.020735 | -0.010422 | 0.098236 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 105.1867 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C04 (hidden)
C04 | Drive row | 38490.0179 | Isc/Iload | 8 | 8.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.955 | PF
6 Pulse | 33 |  | 10 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 8 | 10 | 2 | 0.001299 | 8.0026
link choke | 1 | 9 | 10 |  |  | 100 | 0 | Ifund
| 2 | 0.012572 | 0.026363 | 0.013791 | 1.7915e-05 | 0.01259 | 0
3% AC | 3 | 2.8653 | 1.9764 | -0.88883 | -0.0011546 | 2.8641 | 0
reactor | 4 | 0.014672 | 0.0034978 | -0.011174 | -1.4516e-05 | 0.014658 | 0
| 5 | 29.8339 | 26.8294 | -3.0045 | -0.0039029 | 29.83 | 0
| 6 | 0.007333 | 0.0049368 | -0.0023962 | -3.1128e-06 | 0.0073299 | 0
| 7 | 6.8023 | 6.5167 | -0.2856 | -0.000371 | 6.8019 | 0
| 8 | 0.0043474 | 0.0025416 | -0.0018058 | -2.3458e-06 | 0.004345 | 0
| 9 | 0.5061 | 0.31868 | -0.18742 | -0.00024347 | 0.50586 | 0
| 10 | 0.00095446 | 0.0059001 | 0.0049456 | 6.4246e-06 | 0.00096089 | 0
| 11 | 5.6151 | 4.7731 | -0.842 | -0.0010938 | 5.614 | 0
| 12 | 0.0028138 | 0.0033388 | 0.00052503 | 6.8203e-07 | 0.0028144 | 0
| 13 | 3.1114 | 2.9414 | -0.17004 | -0.00022089 | 3.1112 | 0
| 14 | 0.0067573 | 0.0060541 | -0.00070322 | -9.1351e-07 | 0.0067564 | 0
| 15 | 0.24591 | 0.17864 | -0.06727 | -8.7386e-05 | 0.24582 | 0
| 16 | 0.0049258 | 0.0015412 | -0.0033846 | -4.3967e-06 | 0.0049214 | 0
| 17 | 1.8506 | 1.5325 | -0.31808 | -0.0004132 | 1.8502 | 0
| 18 | 0.0034208 | 0.0023022 | -0.0011186 | -1.4531e-06 | 0.0034193 | 0
| 19 | 1.5015 | 1.1979 | -0.30363 | -0.00039443 | 1.5011 | 0
| 20 | 0.0039991 | 0.0042899 | 0.00029086 | 3.7784e-07 | 0.0039994 | 0
| 21 | 0.20144 | 0.14886 | -0.052576 | -6.8298e-05 | 0.20137 | 0
| 22 | 0.0028423 | 0.0017693 | -0.001073 | -1.3938e-06 | 0.0028409 | 0
| 23 | 0.98669 | 0.97152 | -0.015169 | -1.9705e-05 | 0.98667 | 0
| 24 | 0.0031075 | 0.0016642 | -0.0014433 | -1.8749e-06 | 0.0031057 | 0
| 25 | 0.68094 | 0.60411 | -0.076836 | -9.9813e-05 | 0.68084 | 0
| 26 | 0.0063587 | 0.0057283 | -0.00063035 | -8.1884e-07 | 0.0063579 | 0
| 27 | 0.15761 | 0.099377 | -0.058228 | -7.564e-05 | 0.15753 | 0
| 28 | 0.003309 | 0.0008443 | -0.0024647 | -3.2018e-06 | 0.0033058 | 0
| 29 | 0.72479 | 0.61841 | -0.10638 | -0.00013819 | 0.72465 | 0
| 30 | 0.0028718 | 0.0026822 | -0.00018958 | -2.4627e-07 | 0.0028715 | 0
| 31 | 0.43057 | 0.43268 | 0.0021114 | 2.7427e-06 | 0.43057 | 0
| 32 | 0.0059188 | 0.0045875 | -0.0013313 | -1.7294e-06 | 0.005917 | 0
| 33 | 0.11559 | 0.084151 | -0.031438 | -4.0839e-05 | 0.11555 | 0
| 34 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 35 | 0.48796 | 0.39029 | -0.097671 | -0.00012688 | 0.48784 | 0
| 36 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 37 | 0.31458 | 0.26039 | -0.054192 | -7.0398e-05 | 0.31451 | 0
| 38 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 39 | 0.098387 | 0.071958 | -0.026429 | -3.4333e-05 | 0.098353 | 0
| 40 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 41 | 0.3244 | 0.3053 | -0.019102 | -2.4815e-05 | 0.32438 | 0
| 42 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 43 | 0.19779 | 0.1877 | -0.010089 | -1.3105e-05 | 0.19778 | 0
| 44 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 45 | 0.087933 | 0.058262 | -0.029671 | -3.8544e-05 | 0.087894 | 0
| 46 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 47 | 0.26065 | 0.23679 | -0.023852 | -3.0985e-05 | 0.26061 | 0
| 48 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
| 49 | 0.14568 | 0.14317 | -0.0025146 | -3.2665e-06 | 0.14568 | 0
| 50 | 0.087922 | 0.058256 | -0.029665 | -3.8537e-05 | 0.087883 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 104.8541 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C05 (hidden)
C05 | Drive row | 38490.0179 | Isc/Iload | 10 | 10.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.95 | PF
6 Pulse | 34 |  | 11 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 10 | 12 | 2 | 0.001299 | 10.0026
link choke | 1 | 10 | 11 |  |  | 100 | 0 | Ifund
| 2 | 0.026363 | 0.0039069 | -0.022456 | -2.9171e-05 | 0.026334 | 0
5% AC | 3 | 1.9764 | 1.513 | -0.46344 | -0.00060202 | 1.9758 | 0
reactor | 4 | 0.0034978 | 0.0033184 | -0.00017938 | -2.3302e-07 | 0.0034975 | 0
| 5 | 26.8294 | 24.5244 | -2.3051 | -0.0029944 | 26.8265 | 0
| 6 | 0.0049368 | 0.0021006 | -0.0028362 | -3.6844e-06 | 0.0049331 | 0
| 7 | 6.5167 | 6.6274 | 0.11072 | 0.00014382 | 6.5168 | 0
| 8 | 0.0025416 | 0.0012217 | -0.0013199 | -1.7146e-06 | 0.0025399 | 0
| 9 | 0.31868 | 0.22627 | -0.092415 | -0.00012005 | 0.31856 | 0
| 10 | 0.0059001 | 0.002841 | -0.0030591 | -3.9738e-06 | 0.0058961 | 0
| 11 | 4.7731 | 4.0377 | -0.73537 | -0.00095528 | 4.7722 | 0
| 12 | 0.0033388 | 0.00070415 | -0.0026346 | -3.4225e-06 | 0.0033354 | 0
| 13 | 2.9414 | 2.6891 | -0.25226 | -0.0003277 | 2.9411 | 0
| 14 | 0.0060541 | 0.00088566 | -0.0051685 | -6.714e-06 | 0.0060474 | 0
| 15 | 0.17864 | 0.15239 | -0.026252 | -3.4102e-05 | 0.1786 | 0
| 16 | 0.0015412 | 0.0017707 | 0.00022949 | 2.9812e-07 | 0.0015415 | 0
| 17 | 1.5325 | 1.4252 | -0.10731 | -0.0001394 | 1.5323 | 0
| 18 | 0.0023022 | 0.00071767 | -0.0015845 | -2.0584e-06 | 0.0023002 | 0
| 19 | 1.1979 | 0.96493 | -0.23294 | -0.0003026 | 1.1976 | 0
| 20 | 0.0042899 | 0.0023631 | -0.0019268 | -2.503e-06 | 0.0042874 | 0
| 21 | 0.14886 | 0.11057 | -0.03829 | -4.974e-05 | 0.14881 | 0
| 22 | 0.0017693 | 0.0023684 | 0.00059908 | 7.7823e-07 | 0.0017701 | 0
| 23 | 0.97152 | 0.91499 | -0.056528 | -7.3432e-05 | 0.97145 | 0
| 24 | 0.0016642 | 0.00050466 | -0.0011595 | -1.5063e-06 | 0.0016627 | 0
| 25 | 0.60411 | 0.59625 | -0.0078562 | -1.0206e-05 | 0.6041 | 0
| 26 | 0.0057283 | 0.0014156 | -0.0043127 | -5.6024e-06 | 0.0057227 | 0
| 27 | 0.099377 | 0.075392 | -0.023985 | -3.1158e-05 | 0.099346 | 0
| 28 | 0.0008443 | 0.0017537 | 0.00090938 | 1.1813e-06 | 0.00084548 | 0
| 29 | 0.61841 | 0.50579 | -0.11262 | -0.0001463 | 0.61826 | 0
| 30 | 0.0026822 | 0.00053985 | -0.0021423 | -2.783e-06 | 0.0026794 | 0
| 31 | 0.43268 | 0.37618 | -0.056505 | -7.3402e-05 | 0.43261 | 0
| 32 | 0.0045875 | 0.00127 | -0.0033175 | -4.3096e-06 | 0.0045832 | 0
| 33 | 0.084151 | 0.067504 | -0.016648 | -2.1626e-05 | 0.08413 | 0
| 34 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 35 | 0.39029 | 0.36343 | -0.026859 | -3.489e-05 | 0.39026 | 0
| 36 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 37 | 0.26039 | 0.23294 | -0.027452 | -3.5662e-05 | 0.26035 | 0
| 38 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 39 | 0.071958 | 0.051367 | -0.020591 | -2.6749e-05 | 0.071931 | 0
| 40 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 41 | 0.3053 | 0.27286 | -0.032442 | -4.2144e-05 | 0.30526 | 0
| 42 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 43 | 0.1877 | 0.18025 | -0.0074551 | -9.6844e-06 | 0.18769 | 0
| 44 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 45 | 0.058262 | 0.044255 | -0.014007 | -1.8195e-05 | 0.058243 | 0
| 46 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 47 | 0.23679 | 0.19038 | -0.046409 | -6.0287e-05 | 0.23673 | 0
| 48 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
| 49 | 0.14317 | 0.11821 | -0.024956 | -3.2419e-05 | 0.14313 | 0
| 50 | 0.058256 | 0.044253 | -0.014003 | -1.8191e-05 | 0.058238 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 103.9411 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C06 (hidden)
C06 | Drive row | 38490.0179 | Isc/Iload | 12 | 12.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.95 | PF
6 Pulse | 35 |  | 12 | 0.0025981 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 12 | 14 | 2 | 0.001299 | 12.0026
link choke | 1 | 11 | 12 |  |  | 100 | 0 | Ifund
| 2 | 0.0039069 | 0.017832 | 0.013925 | 1.809e-05 | 0.003925 | 0
7% AC | 3 | 1.513 | 1.248 | -0.265 | -0.00034425 | 1.5126 | 0
reactor | 4 | 0.0033184 | 0.01838 | 0.015062 | 1.9566e-05 | 0.003338 | 0
| 5 | 24.5244 | 22.6661 | -1.8582 | -0.0024139 | 24.522 | 0
| 6 | 0.0021006 | 0.0092816 | 0.0071811 | 9.3285e-06 | 0.0021099 | 0
| 7 | 6.6274 | 6.8022 | 0.17485 | 0.00022714 | 6.6276 | 0
| 8 | 0.0012217 | 0.0064595 | 0.0052379 | 6.8042e-06 | 0.0012285 | 0
| 9 | 0.22627 | 0.17898 | -0.047287 | -6.1427e-05 | 0.2262 | 0
| 10 | 0.002841 | 0.0030933 | 0.00025228 | 3.2772e-07 | 0.0028414 | 0
| 11 | 4.0377 | 3.4442 | -0.59354 | -0.00077103 | 4.037 | 0
| 12 | 0.00070415 | 0.0032867 | 0.0025825 | 3.3548e-06 | 0.00070751 | 0
| 13 | 2.6891 | 2.4129 | -0.27623 | -0.00035883 | 2.6888 | 0
| 14 | 0.00088566 | 0.0045856 | 0.0037 | 4.8064e-06 | 0.00089047 | 0
| 15 | 0.15239 | 0.1388 | -0.01359 | -1.7654e-05 | 0.15237 | 0
| 16 | 0.0017707 | 0.0038905 | 0.0021198 | 2.7537e-06 | 0.0017735 | 0
| 17 | 1.4252 | 1.4118 | -0.013412 | -1.7422e-05 | 1.4252 | 0
| 18 | 0.00071767 | 0.0016748 | 0.00095713 | 1.2433e-06 | 0.00071891 | 0
| 19 | 0.96493 | 0.86231 | -0.10263 | -0.00013332 | 0.9648 | 0
| 20 | 0.0023631 | 0.0020372 | -0.00032592 | -4.2339e-07 | 0.0023627 | 0
| 21 | 0.11057 | 0.08691 | -0.023661 | -3.0737e-05 | 0.11054 | 0
| 22 | 0.0023684 | 0.0022688 | -9.9622e-05 | -1.2941e-07 | 0.0023683 | 0
| 23 | 0.91499 | 0.81941 | -0.095579 | -0.00012416 | 0.91487 | 0
| 24 | 0.00050466 | 0.0024653 | 0.0019606 | 2.5469e-06 | 0.00050721 | 0
| 25 | 0.59625 | 0.57911 | -0.01714 | -2.2265e-05 | 0.59623 | 0
| 26 | 0.0014156 | 0.0023592 | 0.0009436 | 1.2258e-06 | 0.0014169 | 0
| 27 | 0.075392 | 0.068011 | -0.0073801 | -9.5871e-06 | 0.075382 | 0
| 28 | 0.0017537 | 0.0012486 | -0.00050504 | -6.5606e-07 | 0.001753 | 0
| 29 | 0.50579 | 0.46727 | -0.038517 | -5.0035e-05 | 0.50574 | 0
| 30 | 0.00053985 | 0.0008619 | 0.00032205 | 4.1835e-07 | 0.00054027 | 0
| 31 | 0.37618 | 0.31679 | -0.05939 | -7.7149e-05 | 0.3761 | 0
| 32 | 0.00127 | 0.0022444 | 0.00097446 | 1.2659e-06 | 0.0012712 | 0
| 33 | 0.067504 | 0.056413 | -0.01109 | -1.4407e-05 | 0.067489 | 0
| 34 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 35 | 0.36343 | 0.35167 | -0.011768 | -1.5288e-05 | 0.36342 | 0
| 36 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 37 | 0.23294 | 0.23495 | 0.0020158 | 2.6187e-06 | 0.23294 | 0
| 38 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 39 | 0.051367 | 0.04285 | -0.0085165 | -1.1063e-05 | 0.051356 | 0
| 40 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 41 | 0.27286 | 0.23528 | -0.037574 | -4.881e-05 | 0.27281 | 0
| 42 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 43 | 0.18025 | 0.14969 | -0.030554 | -3.969e-05 | 0.18021 | 0
| 44 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 45 | 0.044255 | 0.039512 | -0.0047432 | -6.1616e-06 | 0.044249 | 0
| 46 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 47 | 0.19038 | 0.18456 | -0.005824 | -7.5656e-06 | 0.19038 | 0
| 48 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
| 49 | 0.11821 | 0.11325 | -0.0049632 | -6.4474e-06 | 0.1182 | 0
| 50 | 0.044253 | 0.03951 | -0.0047433 | -6.1617e-06 | 0.044247 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 103.3251 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C07 (hidden)
C07 | Drive row | 38490.0179 | Isc/Iload | 15 | 15.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.945 | PF
6 Pulse | 36 |  | 13 | 1.0026 |  |  |  |  | 0 | Harmonic multiplier
5% DC |  | 14 | 18 | 4 | 0.25065 | 15.0026
link choke | 1 | 12 | 13 |  |  | 100 | 0 | Ifund
| 2 | 0.017832 | 0.0065715 | -0.011261 | -0.0028225 | 0.01501 | 0
10% AC | 3 | 1.248 | 0.90186 | -0.34612 | -0.086756 | 1.1612 | 0
reactor | 4 | 0.01838 | 0.005724 | -0.012656 | -0.0031722 | 0.015208 | 0
| 5 | 22.6661 | 19.6835 | -2.9827 | -0.7476 | 21.9185 | 0
| 6 | 0.0092816 | 0.0038022 | -0.0054794 | -0.0013734 | 0.0079082 | 0
| 7 | 6.8022 | 6.9872 | 0.18499 | 0.046368 | 6.8486 | 0
| 8 | 0.0064595 | 0.0013984 | -0.0050612 | -0.0012686 | 0.005191 | 0
| 9 | 0.17898 | 0.13966 | -0.039319 | -0.0098553 | 0.16912 | 0
| 10 | 0.0030933 | 0.0017025 | -0.0013908 | -0.00034861 | 0.0027447 | 0
| 11 | 3.4442 | 2.6571 | -0.7871 | -0.19729 | 3.2469 | 0
| 12 | 0.0032867 | 0.0021299 | -0.0011568 | -0.00028994 | 0.0029967 | 0
| 13 | 2.4129 | 1.9019 | -0.511 | -0.12808 | 2.2848 | 0
| 14 | 0.0045856 | 0.0023769 | -0.0022087 | -0.00055362 | 0.004032 | 0
| 15 | 0.1388 | 0.1085 | -0.030297 | -0.0075938 | 0.1312 | 0
| 16 | 0.0038905 | 0.003127 | -0.00076354 | -0.00019138 | 0.0036992 | 0
| 17 | 1.4118 | 1.3486 | -0.063183 | -0.015837 | 1.3959 | 0
| 18 | 0.0016748 | 0.0010243 | -0.00065046 | -0.00016304 | 0.0015118 | 0
| 19 | 0.86231 | 0.87143 | 0.009126 | 0.0022874 | 0.86459 | 0
| 20 | 0.0020372 | 0.0026099 | 0.00057272 | 0.00014355 | 0.0021808 | 0
| 21 | 0.08691 | 0.064698 | -0.022211 | -0.0055672 | 0.081342 | 0
| 22 | 0.0022688 | 0.0032957 | 0.0010269 | 0.0002574 | 0.0025262 | 0
| 23 | 0.81941 | 0.64151 | -0.1779 | -0.044591 | 0.77482 | 0
| 24 | 0.0024653 | 0.00056816 | -0.0018971 | -0.00047551 | 0.0019898 | 0
| 25 | 0.57911 | 0.47588 | -0.10323 | -0.025875 | 0.55324 | 0
| 26 | 0.0023592 | 0.0030481 | 0.00068888 | 0.00017267 | 0.0025319 | 0
| 27 | 0.068011 | 0.055666 | -0.012345 | -0.0030943 | 0.064917 | 0
| 28 | 0.0012486 | 0.0032293 | 0.0019807 | 0.00049646 | 0.0017451 | 0
| 29 | 0.46727 | 0.45387 | -0.013403 | -0.0033594 | 0.46391 | 0
| 30 | 0.0008619 | 0.00070588 | -0.00015602 | -3.9106e-05 | 0.00082279 | 0
| 31 | 0.31679 | 0.30877 | -0.0080157 | -0.0020091 | 0.31478 | 0
| 32 | 0.0022444 | 0.0028385 | 0.00059407 | 0.0001489 | 0.0023933 | 0
| 33 | 0.056413 | 0.041648 | -0.014766 | -0.003701 | 0.052712 | 0
| 34 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 35 | 0.35167 | 0.28545 | -0.066214 | -0.016596 | 0.33507 | 0
| 36 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 37 | 0.23495 | 0.19831 | -0.036643 | -0.0091846 | 0.22577 | 0
| 38 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 39 | 0.04285 | 0.035922 | -0.0069278 | -0.0017364 | 0.041114 | 0
| 40 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 41 | 0.23528 | 0.2193 | -0.01598 | -0.0040053 | 0.23128 | 0
| 42 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 43 | 0.14969 | 0.15402 | 0.0043282 | 0.0010849 | 0.15078 | 0
| 44 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 45 | 0.039512 | 0.029543 | -0.0099686 | -0.0024986 | 0.037013 | 0
| 46 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 47 | 0.18456 | 0.16109 | -0.023476 | -0.0058841 | 0.17868 | 0
| 48 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
| 49 | 0.11325 | 0.10592 | -0.0073271 | -0.0018365 | 0.11141 | 0
| 50 | 0.03951 | 0.029543 | -0.0099671 | -0.0024983 | 0.037012 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 102.7069 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.017291 | 0.066998 | 0.12417 | 0.19165 | 0.032432 | 0.026795 | 0.010787 | 0.015489 | 0.011121 | 0.012572 | 0.026363 | 0.0039069 | 0.017832 | 0.0065715 | 0.0057146 | 0.0057146 | 0.0057146 | 0.0057146
3 |  |  | 0.55385 | 8.5474 | 4.3858 | 4.8917 | 5.1072 | 6.2073 | 7.7609 | 5.1366 | 3.7115 | 2.8653 | 1.9764 | 1.513 | 1.248 | 0.90186 | 0.86112 | 0.86112 | 0.86112 | 0.86112
4 |  |  | 0.1352 | 0.028695 | 0.11238 | 0.12707 | 0.029674 | 0.021212 | 0.018917 | 0.024592 | 0.02231 | 0.014672 | 0.0034978 | 0.0033184 | 0.01838 | 0.005724 | 0.0015848 | 0.0015848 | 0.0015848 | 0.0015848
5 |  |  | 93.3687 | 82.8768 | 73.2472 | 60.8315 | 49.3828 | 41.7275 | 37.2795 | 34.2404 | 31.8018 | 29.8339 | 26.8294 | 24.5244 | 22.6661 | 19.6835 | 19.5542 | 19.5542 | 19.5542 | 19.5542
6 |  |  | 0.068818 | 0.052936 | 0.0070103 | 0.011862 | 0.0019223 | 0.011087 | 0.0067285 | 0.0045195 | 0.006017 | 0.007333 | 0.0049368 | 0.0021006 | 0.0092816 | 0.0038022 | 0.0026949 | 0.0026949 | 0.0026949 | 0.0026949
7 |  |  | 85.7929 | 65.6754 | 52.4711 | 34.4739 | 20.7048 | 13.8859 | 10.4074 | 8.4234 | 7.3447 | 6.8023 | 6.5167 | 6.6274 | 6.8022 | 6.9872 | 7.326 | 7.326 | 7.326 | 7.326
8 |  |  | 0.15207 | 0.052892 | 0.05704 | 0.019116 | 0.023565 | 0.0085355 | 0.019604 | 0.012637 | 0.010643 | 0.0043474 | 0.0025416 | 0.0012217 | 0.0064595 | 0.0013984 | 0.0034056 | 0.0034056 | 0.0034056 | 0.0034056
9 |  |  | 1.1544 | 3.5915 | 0.66157 | 0.60369 | 0.42448 | 1.0649 | 1.5533 | 0.98716 | 0.68104 | 0.5061 | 0.31868 | 0.22627 | 0.17898 | 0.13966 | 0.13247 | 0.13247 | 0.13247 | 0.13247
10 |  |  | 0.2294 | 0.046741 | 0.039171 | 0.031896 | 0.0097073 | 0.01376 | 0.012351 | 0.0078771 | 0.0066241 | 0.00095446 | 0.0059001 | 0.002841 | 0.0030933 | 0.0017025 | 0.0038405 | 0.0038405 | 0.0038405 | 0.0038405
11 |  |  | 69.0486 | 33.6853 | 15.5838 | 6.5636 | 7.6798 | 7.4571 | 6.9056 | 6.5341 | 6.0786 | 5.6151 | 4.7731 | 4.0377 | 3.4442 | 2.6571 | 2.6319 | 2.6319 | 2.6319 | 2.6319
12 |  |  | 0.043926 | 0.012877 | 0.0045954 | 0.0053292 | 0.0017456 | 0.0061922 | 0.004634 | 0.0012659 | 0.00072345 | 0.0028138 | 0.0033388 | 0.00070415 | 0.0032867 | 0.0021299 | 0.0030726 | 0.0030726 | 0.0030726 | 0.0030726
13 |  |  | 57.6261 | 19.0088 | 6.0811 | 6.4204 | 4.0538 | 3.1368 | 3.2688 | 3.1927 | 3.159 | 3.1114 | 2.9414 | 2.6891 | 2.4129 | 1.9019 | 1.9731 | 1.9731 | 1.9731 | 1.9731
14 |  |  | 0.20927 | 0.055603 | 0.040151 | 0.011364 | 0.015809 | 0.011301 | 0.013986 | 0.013727 | 0.012923 | 0.0067573 | 0.0060541 | 0.00088566 | 0.0045856 | 0.0023769 | 0.0021688 | 0.0021688 | 0.0021688 | 0.0021688
15 |  |  | 1.1369 | 0.23096 | 0.45935 | 0.33979 | 0.19878 | 0.61174 | 0.77397 | 0.4769 | 0.32445 | 0.24591 | 0.17864 | 0.15239 | 0.1388 | 0.1085 | 0.10439 | 0.10439 | 0.10439 | 0.10439
16 |  |  | 0.2126 | 0.055251 | 0.029549 | 0.019149 | 0.0088894 | 0.0098005 | 0.0093355 | 0.011177 | 0.010798 | 0.0049258 | 0.0015412 | 0.0017707 | 0.0038905 | 0.003127 | 0.0027547 | 0.0027547 | 0.0027547 | 0.0027547
17 |  |  | 38.3059 | 5.3 | 6.2578 | 3.6516 | 3.9361 | 3.5366 | 2.7955 | 2.4617 | 2.1281 | 1.8506 | 1.5325 | 1.4252 | 1.4118 | 1.3486 | 1.3517 | 1.3517 | 1.3517 | 1.3517
18 |  |  | 0.0068073 | 0.0044855 | 0.003708 | 0.0041892 | 0.0025801 | 0.0051323 | 0.0032625 | 0.00097249 | 0.00053825 | 0.0034208 | 0.0023022 | 0.00071767 | 0.0016748 | 0.0010243 | 0.0027646 | 0.0027646 | 0.0027646 | 0.0027646
19 |  |  | 28.1268 | 5.7694 | 4.4923 | 2.4618 | 1.5612 | 1.4353 | 1.8153 | 1.7533 | 1.6441 | 1.5015 | 1.1979 | 0.96493 | 0.86231 | 0.87143 | 0.89424 | 0.89424 | 0.89424 | 0.89424
20 |  |  | 0.16228 | 0.034305 | 0.036035 | 0.013414 | 0.013821 | 0.012554 | 0.011519 | 0.012483 | 0.01066 | 0.0039991 | 0.0042899 | 0.0023631 | 0.0020372 | 0.0026099 | 0.0033164 | 0.0033164 | 0.0033164 | 0.0033164
21 |  |  | 0.62329 | 0.38653 | 0.28849 | 0.23276 | 0.12696 | 0.43157 | 0.51233 | 0.3364 | 0.24976 | 0.20144 | 0.14886 | 0.11057 | 0.08691 | 0.064698 | 0.062073 | 0.062073 | 0.062073 | 0.062073
22 |  |  | 0.10197 | 0.038702 | 0.032941 | 0.014397 | 0.0080433 | 0.0091411 | 0.013328 | 0.0099334 | 0.0087777 | 0.0028423 | 0.0017693 | 0.0023684 | 0.0022688 | 0.0032957 | 0.0031846 | 0.0031846 | 0.0031846 | 0.0031846
23 |  |  | 14.1113 | 4.5503 | 2.8173 | 2.0671 | 2.2928 | 1.9472 | 1.3645 | 1.1709 | 1.045 | 0.98669 | 0.97152 | 0.91499 | 0.81941 | 0.64151 | 0.64347 | 0.64347 | 0.64347 | 0.64347
24 |  |  | 0.036824 | 0.0098383 | 0.0024869 | 0.0037823 | 0.0030036 | 0.0053235 | 0.0058117 | 0.0029855 | 0.0023273 | 0.0031075 | 0.0016642 | 0.00050466 | 0.0024653 | 0.00056816 | 0.0029101 | 0.0029101 | 0.0029101 | 0.0029101
25 |  |  | 9.1461 | 3.3288 | 2.4769 | 1.4066 | 0.98125 | 0.87517 | 1.0203 | 0.89182 | 0.77335 | 0.68094 | 0.60411 | 0.59625 | 0.57911 | 0.47588 | 0.48333 | 0.48333 | 0.48333 | 0.48333
26 |  |  | 0.050822 | 0.055063 | 0.02657 | 0.017181 | 0.014414 | 0.013401 | 0.012262 | 0.011494 | 0.011502 | 0.0063587 | 0.0057283 | 0.0014156 | 0.0023592 | 0.0030481 | 0.0025058 | 0.0025058 | 0.0025058 | 0.0025058
27 |  |  | 0.21239 | 0.25707 | 0.16074 | 0.17381 | 0.091194 | 0.33088 | 0.40809 | 0.28326 | 0.20564 | 0.15761 | 0.099377 | 0.075392 | 0.068011 | 0.055666 | 0.053355 | 0.053355 | 0.053355 | 0.053355
28 |  |  | 0.019393 | 0.047103 | 0.028971 | 0.011873 | 0.0069611 | 0.0085363 | 0.012557 | 0.010538 | 0.0092931 | 0.003309 | 0.0008443 | 0.0017537 | 0.0012486 | 0.0032293 | 0.0027334 | 0.0027334 | 0.0027334 | 0.0027334
29 |  |  | 6.5147 | 2.6788 | 1.6107 | 1.3975 | 1.4 | 1.0908 | 0.75871 | 0.75679 | 0.75576 | 0.72479 | 0.61841 | 0.50579 | 0.46727 | 0.45387 | 0.45143 | 0.45143 | 0.45143 | 0.45143
30 |  |  | 0.034884 | 0.0041766 | 0.0031946 | 0.0036029 | 0.003292 | 0.0050315 | 0.0046053 | 0.0036992 | 0.0019564 | 0.0028718 | 0.0026822 | 0.00053985 | 0.0008619 | 0.00070588 | 0.0025967 | 0.0025967 | 0.0025967 | 0.0025967
31 |  |  | 6.3339 | 2.4859 | 1.4322 | 0.8228 | 0.68512 | 0.58112 | 0.56773 | 0.46222 | 0.42487 | 0.43057 | 0.43268 | 0.37618 | 0.31679 | 0.30877 | 0.31207 | 0.31207 | 0.31207 | 0.31207
32 |  |  | 0.046506 | 0.033261 | 0.029586 | 0.019536 | 0.014564 | 0.013059 | 0.0088971 | 0.011901 | 0.011922 | 0.0059188 | 0.0045875 | 0.00127 | 0.0022444 | 0.0028385 | 0.0029287 | 0.0029287 | 0.0029287 | 0.0029287
33 |  |  | 0.30275 | 0.017217 | 0.12234 | 0.13606 | 0.070763 | 0.26564 | 0.34166 | 0.22742 | 0.15382 | 0.11559 | 0.084151 | 0.067504 | 0.056413 | 0.041648 | 0.0398 | 0.0398 | 0.0398 | 0.0398
34 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
35 |  |  | 5.903 | 1.4733 | 1.2804 | 1.029 | 0.95079 | 0.68756 | 0.51648 | 0.56585 | 0.55172 | 0.48796 | 0.39029 | 0.36343 | 0.35167 | 0.28545 | 0.28282 | 0.28282 | 0.28282 | 0.28282
36 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
37 |  |  | 4.7243 | 1.4148 | 0.86563 | 0.58792 | 0.44571 | 0.35071 | 0.34192 | 0.32136 | 0.32334 | 0.31458 | 0.26039 | 0.23294 | 0.23495 | 0.19831 | 0.19996 | 0.19996 | 0.19996 | 0.19996
38 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
39 |  |  | 0.20799 | 0.13042 | 0.12948 | 0.11009 | 0.060149 | 0.2195 | 0.27641 | 0.17818 | 0.12256 | 0.098387 | 0.071958 | 0.051367 | 0.04285 | 0.035922 | 0.034556 | 0.034556 | 0.034556 | 0.034556
40 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
41 |  |  | 2.9594 | 1.396 | 0.97885 | 0.76627 | 0.64986 | 0.49479 | 0.39951 | 0.41595 | 0.37579 | 0.3244 | 0.3053 | 0.27286 | 0.23528 | 0.2193 | 0.21942 | 0.21942 | 0.21942 | 0.21942
42 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
43 |  |  | 2.2179 | 1.1906 | 0.75615 | 0.45363 | 0.28528 | 0.2178 | 0.25539 | 0.24819 | 0.22309 | 0.19779 | 0.1877 | 0.18025 | 0.14969 | 0.15402 | 0.14788 | 0.14788 | 0.14788 | 0.14788
44 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
45 |  |  | 0.15674 | 0.069136 | 0.11722 | 0.090976 | 0.055975 | 0.18455 | 0.21867 | 0.14808 | 0.10867 | 0.087933 | 0.058262 | 0.044255 | 0.039512 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
46 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
47 |  |  | 2.3269 | 0.78641 | 0.65684 | 0.58143 | 0.44929 | 0.41294 | 0.29406 | 0.27869 | 0.26697 | 0.26065 | 0.23679 | 0.19038 | 0.18456 | 0.16109 | 0.15522 | 0.15522 | 0.15522 | 0.15522
48 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
49 |  |  | 2.2221 | 0.82313 | 0.54373 | 0.33389 | 0.20473 | 0.16068 | 0.19636 | 0.18022 | 0.15241 | 0.14568 | 0.14317 | 0.11821 | 0.11325 | 0.10592 | 0.10181 | 0.10181 | 0.10181 | 0.10181
50 |  |  | 0.15658 | 0.069206 | 0.1172 | 0.090951 | 0.056069 | 0.18458 | 0.21861 | 0.14805 | 0.10866 | 0.087922 | 0.058256 | 0.044253 | 0.03951 | 0.029543 | 0.028072 | 0.028072 | 0.028072 | 0.028072
| Ithd |  | 163.9377 | 113.488 | 92.2015 | 70.9141 | 54.7501 | 45.4091 | 40.4528 | 36.5676 | 33.7225 | 31.5378 | 28.3536 | 26.004 | 24.1602 | 21.2497 | 21.2472 | 21.2472 | 21.2472 | 21.2472

## C08 (hidden)
C08 | Drive row | 38490.0179 | Isc/Iload | 5 | 5.0026 | %Z | 0 | A | 0 | PU Load |  |  | 0.995 | PF | kW/kVA
6 Pulse | 37 |  | 7 | 0.0025981 |  |  |  |  | 0.1475 | Harmonic multiplier
5% DC |  | 5 | 6 | 1 | 0.0025981 | 5.0026 | [6 empty] | -0.099875 | QF | kVAR/kVA
link choke | 1 | 6 | 7 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.2862 | 0.2862 | 0 | 0 | 0.2862 | 0 |  | 0 | actual hp
7% THDi | 3 | 0.039331 | 0.039331 | 0 | 0 | 0.039331 | 0
filter | 4 | 0.25832 | 0.25832 | 0 | 0 | 0.25832 | 0 |  | -35 | Ifilter at no load, 100hp
| 5 | 4.5719 | 4.5719 | 0 | 0 | 4.5719 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.017666 | 0.017666 | 0 | 0 | 0.017666 | 0
| 7 | 3.2679 | 3.2679 | 0 | 0 | 3.2679 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.017088 | 0.017088 | 0 | 0 | 0.017088 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.0083557 | 0.0083557 | 0 | 0 | 0.0083557 | 0 |  | 0 | Ireact at xpu
| 10 | 0.0047045 | 0.0047045 | 0 | 0 | 0.0047045 | 0
| 11 | 3.0368 | 3.0368 | 0 | 0 | 3.0368 | 0 |  | 0 | Ireal at 1pu
| 12 | 0.0029416 | 0.0029416 | 0 | 0 | 0.0029416 | 0 |  | 0 | Ireal at xpu
| 13 | 1.9571 | 1.9571 | 0 | 0 | 1.9571 | 0
| 14 | 0.010432 | 0.010432 | 0 | 0 | 0.010432 | 0 |  | 0 | Ifund at 1pu
| 15 | 0.0019438 | 0.0019438 | 0 | 0 | 0.0019438 | 0 |  | 0 | Ifund at xpu
| 16 | 0.00873 | 0.00873 | 0 | 0 | 0.00873 | 0
| 17 | 0.97557 | 0.97557 | 0 | 0 | 0.97557 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0026049 | 0.0026049 | 0 | 0 | 0.0026049 | 0
| 19 | 0.91669 | 0.91669 | 0 | 0 | 0.91669 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0034359 | 0.0034359 | 0 | 0 | 0.0034359 | 0
| 21 | 0.0015448 | 0.0015448 | 0 | 0 | 0.0015448 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0052235 | 0.0052235 | 0 | 0 | 0.0052235 | 0
| 23 | 0.54728 | 0.54728 | 0 | 0 | 0.54728 | 0
| 24 | 0.00073681 | 0.00073681 | 0 | 0 | 0.00073681 | 0
| 25 | 0.4394 | 0.4394 | 0 | 0 | 0.4394 | 0
| 26 | 0.0037751 | 0.0037751 | 0 | 0 | 0.0037751 | 0
| 27 | 0.0014496 | 0.0014496 | 0 | 0 | 0.0014496 | 0
| 28 | 0.002311 | 0.002311 | 0 | 0 | 0.002311 | 0
| 29 | 0.39633 | 0.39633 | 0 | 0 | 0.39633 | 0
| 30 | 0.0011457 | 0.0011457 | 0 | 0 | 0.0011457 | 0
| 31 | 0.32608 | 0.32608 | 0 | 0 | 0.32608 | 0
| 32 | 0.0038606 | 0.0038606 | 0 | 0 | 0.0038606 | 0
| 33 | 0.00034023 | 0.00034023 | 0 | 0 | 0.00034023 | 0
| 34 | 0.0038157 | 0.0038157 | 0 | 0 | 0.0038157 | 0
| 35 | 0.24452 | 0.24452 | 0 | 0 | 0.24452 | 0
| 36 | 0.0008725 | 0.0008725 | 0 | 0 | 0.0008725 | 0
| 37 | 0.23543 | 0.23543 | 0 | 0 | 0.23543 | 0
| 38 | 0.0016183 | 0.0016183 | 0 | 0 | 0.0016183 | 0
| 39 | 0.00091856 | 0.00091856 | 0 | 0 | 0.00091856 | 0
| 40 | 0.0021859 | 0.0021859 | 0 | 0 | 0.0021859 | 0
| 41 | 0.17547 | 0.17547 | 0 | 0 | 0.17547 | 0
| 42 | 0.00033318 | 0.00033318 | 0 | 0 | 0.00033318 | 0
| 43 | 0.15609 | 0.15609 | 0 | 0 | 0.15609 | 0
| 44 | 0.0025667 | 0.0025667 | 0 | 0 | 0.0025667 | 0
| 45 | 0.00048875 | 0.00048875 | 0 | 0 | 0.00048875 | 0
| 46 | 0.0019607 | 0.0019607 | 0 | 0 | 0.0019607 | 0
| 47 | 0.14695 | 0.14695 | 0 | 0 | 0.14695 | 0
| 48 | 0.00069771 | 0.00069771 | 0 | 0 | 0.00069771 | 0
| 49 | 0.12856 | 0.12856 | 0 | 0 | 0.12856 | 0
| 50 | 0.0019605 | 0.0019605 | 0 | 0 | 0.0019605 | 0
[5 empty] | thd | 6.8951 | 0 | Iharm
[5 empty] | total | 100.2374 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.32933 | 0.31535 | 0.30142 | 0.28744 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862 | 0.2862
3 |  |  | 0.04526 | 0.043339 | 0.041423 | 0.039502 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331 | 0.039331
4 |  |  | 0.29726 | 0.28464 | 0.27206 | 0.25945 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832 | 0.25832
5 |  |  | 5.261 | 5.0377 | 4.8151 | 4.5918 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719 | 4.5719
6 |  |  | 0.020329 | 0.019466 | 0.018605 | 0.017743 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666 | 0.017666
7 |  |  | 3.7605 | 3.6009 | 3.4418 | 3.2822 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679 | 3.2679
8 |  |  | 0.019663 | 0.018829 | 0.017997 | 0.017162 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088 | 0.017088
9 |  |  | 0.0096151 | 0.009207 | 0.0088001 | 0.008392 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557 | 0.0083557
10 |  |  | 0.0054136 | 0.0051838 | 0.0049547 | 0.004725 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045 | 0.0047045
11 |  |  | 3.4945 | 3.3462 | 3.1983 | 3.05 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368 | 3.0368
12 |  |  | 0.0033849 | 0.0032412 | 0.003098 | 0.0029543 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416 | 0.0029416
13 |  |  | 2.2521 | 2.1565 | 2.0612 | 1.9656 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571 | 1.9571
14 |  |  | 0.012004 | 0.011495 | 0.010987 | 0.010477 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432 | 0.010432
15 |  |  | 0.0022368 | 0.0021419 | 0.0020472 | 0.0019523 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438 | 0.0019438
16 |  |  | 0.010046 | 0.0096194 | 0.0091943 | 0.0087679 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873 | 0.00873
17 |  |  | 1.1226 | 1.075 | 1.0275 | 0.97981 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557 | 0.97557
18 |  |  | 0.0029975 | 0.0028703 | 0.0027435 | 0.0026162 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049 | 0.0026049
19 |  |  | 1.0549 | 1.0101 | 0.96545 | 0.92068 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669 | 0.91669
20 |  |  | 0.0039537 | 0.0037859 | 0.0036186 | 0.0034508 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359 | 0.0034359
21 |  |  | 0.0017776 | 0.0017022 | 0.001627 | 0.0015515 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448 | 0.0015448
22 |  |  | 0.0060108 | 0.0057557 | 0.0055013 | 0.0052462 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235 | 0.0052235
23 |  |  | 0.62977 | 0.60304 | 0.57639 | 0.54966 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728 | 0.54728
24 |  |  | 0.00084787 | 0.00081188 | 0.000776 | 0.00074001 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681 | 0.00073681
25 |  |  | 0.50563 | 0.48417 | 0.46277 | 0.44131 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394 | 0.4394
26 |  |  | 0.0043441 | 0.0041597 | 0.0039759 | 0.0037915 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751 | 0.0037751
27 |  |  | 0.0016681 | 0.0015973 | 0.0015267 | 0.0014559 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496 | 0.0014496
28 |  |  | 0.0026594 | 0.0025465 | 0.002434 | 0.0023211 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311 | 0.002311
29 |  |  | 0.45607 | 0.43671 | 0.41741 | 0.39805 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633 | 0.39633
30 |  |  | 0.0013184 | 0.0012624 | 0.0012066 | 0.0011507 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457 | 0.0011457
31 |  |  | 0.37522 | 0.3593 | 0.34342 | 0.32749 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608 | 0.32608
32 |  |  | 0.0044425 | 0.0042539 | 0.0040659 | 0.0038774 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606 | 0.0038606
33 |  |  | 0.00039151 | 0.0003749 | 0.00035833 | 0.00034171 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023 | 0.00034023
34 |  |  | 0.0043909 | 0.0042045 | 0.0040187 | 0.0038323 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157 | 0.0038157
35 |  |  | 0.28137 | 0.26943 | 0.25752 | 0.24558 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452 | 0.24452
36 |  |  | 0.001004 | 0.0009614 | 0.00091891 | 0.0008763 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725 | 0.0008725
37 |  |  | 0.27092 | 0.25942 | 0.24796 | 0.23646 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543 | 0.23543
38 |  |  | 0.0018623 | 0.0017832 | 0.0017044 | 0.0016254 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183 | 0.0016183
39 |  |  | 0.001057 | 0.0010121 | 0.00096741 | 0.00092255 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856 | 0.00091856
40 |  |  | 0.0025154 | 0.0024086 | 0.0023021 | 0.0021954 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859 | 0.0021859
41 |  |  | 0.20192 | 0.19335 | 0.1848 | 0.17623 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547
42 |  |  | 0.0003834 | 0.00036713 | 0.0003509 | 0.00033463 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318 | 0.00033318
43 |  |  | 0.17961 | 0.17199 | 0.16439 | 0.15677 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609 | 0.15609
44 |  |  | 0.0029536 | 0.0028282 | 0.0027032 | 0.0025779 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667 | 0.0025667
45 |  |  | 0.00056241 | 0.00053854 | 0.00051474 | 0.00049087 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875 | 0.00048875
46 |  |  | 0.0022562 | 0.0021605 | 0.002065 | 0.0019692 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607 | 0.0019607
47 |  |  | 0.1691 | 0.16192 | 0.15476 | 0.14759 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695 | 0.14695
48 |  |  | 0.00080287 | 0.00076879 | 0.00073482 | 0.00070074 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771 | 0.00069771
49 |  |  | 0.14794 | 0.14166 | 0.1354 | 0.12912 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856 | 0.12856
50 |  |  | 0.0022559 | 0.0021602 | 0.0020647 | 0.001969 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605 | 0.0019605
| Ithd |  | 7.9343 | 7.5976 | 7.2618 | 6.9251 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951 | 6.8951

## C09 (hidden)
C09 | Drive row | 38490.0179 | Isc/Iload | 5 | 5.0026 | %Z | 0 | FLA | 0 | PU Load |  |  | 0.999 | PF | kW/kVA
6 Pulse | 38 |  | 7 | 0.0025981 |  |  |  |  | 1.1251 | Harmonic multiplier
5% DC |  | 5 | 6 | 1 | 0.0025981 | 5.0026 | [6 empty] | 0.04471 | QF | kVAR/kVA
link choke | 1 | 6 | 7 |  |  | 100 | 0 | Ifund | 0 | rated hp
| 2 | 0.20034 | 0.20034 | 0 | 0 | 0.20034 | 0 |  | 0 | actual hp
5% THDi | 3 | 0.027532 | 0.027532 | 0 | 0 | 0.027532 | 0
filter | 4 | 0.18083 | 0.18083 | 0 | 0 | 0.18083 | 0 |  | -40 | Ifilter at no load, 100hp
| 5 | 3.2003 | 3.2003 | 0 | 0 | 3.2003 | 0 |  | 0 | Ifilter at no load, rated hp
| 6 | 0.012366 | 0.012366 | 0 | 0 | 0.012366 | 0
| 7 | 2.2876 | 2.2876 | 0 | 0 | 2.2876 | 0 |  | 0 | Ireact at 0pu
| 8 | 0.011961 | 0.011961 | 0 | 0 | 0.011961 | 0 |  | 0 | Ireact at 1pu
| 9 | 0.005849 | 0.005849 | 0 | 0 | 0.005849 | 0 |  | 0 | Ireact at xpu
| 10 | 0.0032932 | 0.0032932 | 0 | 0 | 0.0032932 | 0
| 11 | 2.1258 | 2.1258 | 0 | 0 | 2.1258 | 0 |  | 0 | Ireal at 1pu
| 12 | 0.0020591 | 0.0020591 | 0 | 0 | 0.0020591 | 0 |  | 0 | Ireal at xpu
| 13 | 1.37 | 1.37 | 0 | 0 | 1.37 | 0
| 14 | 0.0073022 | 0.0073022 | 0 | 0 | 0.0073022 | 0 |  | 0 | Ifund at 1pu
| 15 | 0.0013607 | 0.0013607 | 0 | 0 | 0.0013607 | 0 |  | 0 | Ifund at xpu
| 16 | 0.006111 | 0.006111 | 0 | 0 | 0.006111 | 0
| 17 | 0.6829 | 0.6829 | 0 | 0 | 0.6829 | 0 |  | 0 | Iharm at xpu
| 18 | 0.0018234 | 0.0018234 | 0 | 0 | 0.0018234 | 0
| 19 | 0.64169 | 0.64169 | 0 | 0 | 0.64169 | 0 |  | 0 | Itotal at xpu
| 20 | 0.0024051 | 0.0024051 | 0 | 0 | 0.0024051 | 0
| 21 | 0.0010814 | 0.0010814 | 0 | 0 | 0.0010814 | 0 |  | 0 | Ithd at xpu
| 22 | 0.0036564 | 0.0036564 | 0 | 0 | 0.0036564 | 0
| 23 | 0.3831 | 0.3831 | 0 | 0 | 0.3831 | 0
| 24 | 0.00051577 | 0.00051577 | 0 | 0 | 0.00051577 | 0
| 25 | 0.30758 | 0.30758 | 0 | 0 | 0.30758 | 0
| 26 | 0.0026426 | 0.0026426 | 0 | 0 | 0.0026426 | 0
| 27 | 0.0010147 | 0.0010147 | 0 | 0 | 0.0010147 | 0
| 28 | 0.0016177 | 0.0016177 | 0 | 0 | 0.0016177 | 0
| 29 | 0.27743 | 0.27743 | 0 | 0 | 0.27743 | 0
| 30 | 0.00080198 | 0.00080198 | 0 | 0 | 0.00080198 | 0
| 31 | 0.22825 | 0.22825 | 0 | 0 | 0.22825 | 0
| 32 | 0.0027024 | 0.0027024 | 0 | 0 | 0.0027024 | 0
| 33 | 0.00023816 | 0.00023816 | 0 | 0 | 0.00023816 | 0
| 34 | 0.002671 | 0.002671 | 0 | 0 | 0.002671 | 0
| 35 | 0.17116 | 0.17116 | 0 | 0 | 0.17116 | 0
| 36 | 0.00061075 | 0.00061075 | 0 | 0 | 0.00061075 | 0
| 37 | 0.1648 | 0.1648 | 0 | 0 | 0.1648 | 0
| 38 | 0.0011328 | 0.0011328 | 0 | 0 | 0.0011328 | 0
| 39 | 0.00064299 | 0.00064299 | 0 | 0 | 0.00064299 | 0
| 40 | 0.0015301 | 0.0015301 | 0 | 0 | 0.0015301 | 0
| 41 | 0.12283 | 0.12283 | 0 | 0 | 0.12283 | 0
| 42 | 0.00023323 | 0.00023323 | 0 | 0 | 0.00023323 | 0
| 43 | 0.10926 | 0.10926 | 0 | 0 | 0.10926 | 0
| 44 | 0.0017967 | 0.0017967 | 0 | 0 | 0.0017967 | 0
| 45 | 0.00034212 | 0.00034212 | 0 | 0 | 0.00034212 | 0
| 46 | 0.0013725 | 0.0013725 | 0 | 0 | 0.0013725 | 0
| 47 | 0.10286 | 0.10286 | 0 | 0 | 0.10286 | 0
| 48 | 0.0004884 | 0.0004884 | 0 | 0 | 0.0004884 | 0
| 49 | 0.089995 | 0.089995 | 0 | 0 | 0.089995 | 0
| 50 | 0.0013723 | 0.0013723 | 0 | 0 | 0.0013723 | 0
[5 empty] | thd | 4.8266 | 0 | Iharm
[5 empty] | total | 100.1164 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.20697 | 0.20519 | 0.20336 | 0.20158 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034 | 0.20034
3 |  |  | 0.028444 | 0.028199 | 0.027948 | 0.027703 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532 | 0.027532
4 |  |  | 0.18682 | 0.18521 | 0.18356 | 0.18195 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083 | 0.18083
5 |  |  | 3.3064 | 3.2779 | 3.2487 | 3.2202 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003 | 3.2003
6 |  |  | 0.012776 | 0.012666 | 0.012553 | 0.012443 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366 | 0.012366
7 |  |  | 2.3633 | 2.343 | 2.3221 | 2.3018 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876 | 2.2876
8 |  |  | 0.012358 | 0.012251 | 0.012142 | 0.012036 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961 | 0.011961
9 |  |  | 0.0060427 | 0.0059906 | 0.0059374 | 0.0058853 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849 | 0.005849
10 |  |  | 0.0034023 | 0.0033729 | 0.0033429 | 0.0033136 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932 | 0.0032932
11 |  |  | 2.1962 | 2.1773 | 2.1579 | 2.139 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258
12 |  |  | 0.0021273 | 0.002109 | 0.0020902 | 0.0020719 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591 | 0.0020591
13 |  |  | 1.4153 | 1.4031 | 1.3907 | 1.3785 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 1.37
14 |  |  | 0.0075441 | 0.0074791 | 0.0074125 | 0.0073475 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022 | 0.0073022
15 |  |  | 0.0014058 | 0.0013936 | 0.0013812 | 0.0013691 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607 | 0.0013607
16 |  |  | 0.0063134 | 0.006259 | 0.0062033 | 0.0061489 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111 | 0.006111
17 |  |  | 0.70552 | 0.69944 | 0.69322 | 0.68714 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829 | 0.6829
18 |  |  | 0.0018838 | 0.0018676 | 0.001851 | 0.0018348 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234 | 0.0018234
19 |  |  | 0.66294 | 0.65723 | 0.65138 | 0.64567 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169
20 |  |  | 0.0024848 | 0.0024634 | 0.0024415 | 0.00242 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051 | 0.0024051
21 |  |  | 0.0011172 | 0.0011075 | 0.0010977 | 0.0010881 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814 | 0.0010814
22 |  |  | 0.0037776 | 0.003745 | 0.0037117 | 0.0036791 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564 | 0.0036564
23 |  |  | 0.39579 | 0.39238 | 0.38889 | 0.38548 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831 | 0.3831
24 |  |  | 0.00053285 | 0.00052826 | 0.00052356 | 0.00051897 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577 | 0.00051577
25 |  |  | 0.31777 | 0.31503 | 0.31223 | 0.30949 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758 | 0.30758
26 |  |  | 0.0027301 | 0.0027066 | 0.0026825 | 0.002659 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426 | 0.0026426
27 |  |  | 0.0010483 | 0.0010393 | 0.00103 | 0.001021 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147 | 0.0010147
28 |  |  | 0.0016713 | 0.0016569 | 0.0016422 | 0.0016278 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177 | 0.0016177
29 |  |  | 0.28662 | 0.28415 | 0.28163 | 0.27916 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743 | 0.27743
30 |  |  | 0.00082855 | 0.00082141 | 0.0008141 | 0.00080696 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198 | 0.00080198
31 |  |  | 0.23581 | 0.23378 | 0.2317 | 0.22967 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825 | 0.22825
32 |  |  | 0.0027919 | 0.0027679 | 0.0027432 | 0.0027192 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024 | 0.0027024
33 |  |  | 0.00024605 | 0.00024393 | 0.00024176 | 0.00023964 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816 | 0.00023816
34 |  |  | 0.0027595 | 0.0027357 | 0.0027114 | 0.0026876 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671 | 0.002671
35 |  |  | 0.17683 | 0.17531 | 0.17375 | 0.17222 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116 | 0.17116
36 |  |  | 0.00063098 | 0.00062555 | 0.00061998 | 0.00061454 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075 | 0.00061075
37 |  |  | 0.17026 | 0.1688 | 0.16729 | 0.16583 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.1648
38 |  |  | 0.0011704 | 0.0011603 | 0.00115 | 0.0011399 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328
39 |  |  | 0.00066429 | 0.00065857 | 0.00065271 | 0.00064698 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299 | 0.00064299
40 |  |  | 0.0015808 | 0.0015672 | 0.0015532 | 0.0015396 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301 | 0.0015301
41 |  |  | 0.1269 | 0.12581 | 0.12469 | 0.12359 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283 | 0.12283
42 |  |  | 0.00024095 | 0.00023888 | 0.00023675 | 0.00023468 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323 | 0.00023323
43 |  |  | 0.11288 | 0.11191 | 0.11091 | 0.10994 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926 | 0.10926
44 |  |  | 0.0018562 | 0.0018402 | 0.0018239 | 0.0018079 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967 | 0.0017967
45 |  |  | 0.00035346 | 0.00035041 | 0.00034729 | 0.00034425 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212 | 0.00034212
46 |  |  | 0.001418 | 0.0014057 | 0.0013932 | 0.001381 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725
47 |  |  | 0.10627 | 0.10536 | 0.10442 | 0.1035 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286
48 |  |  | 0.00050457 | 0.00050023 | 0.00049578 | 0.00049143 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884 | 0.0004884
49 |  |  | 0.092976 | 0.092175 | 0.091355 | 0.090554 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995 | 0.089995
50 |  |  | 0.0014178 | 0.0014056 | 0.0013931 | 0.0013808 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723 | 0.0013723
| Ithd |  | 4.9864 | 4.9435 | 4.8995 | 4.8565 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266 | 4.8266

## D01 (hidden)
D01 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A | 0 | PU Load |  |  | 0.981 | PF disp at Rsc = 30
12 Pulse | 42 |  | 1 | 0 |  |  |  |  | 0 | Harmonic multiplier
|  | 0.1 | 0.5 | 0.4 | 0 | 0.1
| 1 | 0 | 1 |  |  | 100 | 0 | Ifund
| 2 | 0.016734 | 0.0056893 | -0.011045 | 0 | 0.016734 | 0
| 3 | 2.9425 | 2.9912 | 0.0487 | 0 | 2.9425 | 0
| 4 | 0.019268 | 0.032778 | 0.01351 | 0 | 0.019268 | 0
| 5 | 0.0647 | 0.022844 | -0.041856 | 0 | 0.0647 | 0
| 6 | 0.11515 | 0.019737 | -0.095417 | 0 | 0.11515 | 0
| 7 | 0.046424 | 0.041014 | -0.0054099 | 0 | 0.046424 | 0
| 8 | 0.18926 | 0.040911 | -0.14835 | 0 | 0.18926 | 0
| 9 | 2.0675 | 0.47119 | -1.5963 | 0 | 2.0675 | 0
| 10 | 0.099933 | 0.029332 | -0.070601 | 0 | 0.099933 | 0
| 11 | 56.1476 | 21.046 | -35.1016 | 0 | 56.1476 | 0
| 12 | 0.013663 | 0.036627 | 0.022964 | 0 | 0.013663 | 0
| 13 | 45.6948 | 11.0407 | -34.654 | 0 | 45.6948 | 0
| 14 | 0.038701 | 0.032364 | -0.006337 | 0 | 0.038701 | 0
| 15 | 0.70986 | 0.47303 | -0.23683 | 0 | 0.70986 | 0
| 16 | 0.018287 | 0.0091218 | -0.0091656 | 0 | 0.018287 | 0
| 17 | 0.010907 | 0.0086444 | -0.0022627 | 0 | 0.010907 | 0
| 18 | 0.069418 | 0.0082787 | -0.061139 | 0 | 0.069418 | 0
| 19 | 0.0055733 | 0.012693 | 0.0071197 | 0 | 0.0055733 | 0
| 20 | 0.018441 | 0.011776 | -0.0066652 | 0 | 0.018441 | 0
| 21 | 0.027539 | 0.27721 | 0.24967 | 0 | 0.027539 | 0
| 22 | 0.041585 | 0.032859 | -0.0087262 | 0 | 0.041585 | 0
| 23 | 6.5562 | 3.4959 | -3.0603 | 0 | 6.5562 | 0
| 24 | 0.0078956 | 0.031784 | 0.023889 | 0 | 0.0078956 | 0
| 25 | 5.5201 | 3.0355 | -2.4846 | 0 | 5.5201 | 0
| 26 | 0.024335 | 0.026543 | 0.0022087 | 0 | 0.024335 | 0
| 27 | 0.19615 | 0.14918 | -0.046971 | 0 | 0.19615 | 0
| 28 | 0.024676 | 0.0020604 | -0.022616 | 0 | 0.024676 | 0
| 29 | 0.0040788 | 0.010088 | 0.0060095 | 0 | 0.0040788 | 0
| 30 | 0.044163 | 0.0047847 | -0.039378 | 0 | 0.044163 | 0
| 31 | 0.0052247 | 0.0074381 | 0.0022134 | 0 | 0.0052247 | 0
| 32 | 0.033701 | 0.014235 | -0.019466 | 0 | 0.033701 | 0
| 33 | 0.044712 | 0.14987 | 0.10516 | 0 | 0.044712 | 0
| 34 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 35 | 3.4105 | 1.6959 | -1.7147 | 0 | 3.4105 | 0
| 36 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 37 | 2.5783 | 1.3145 | -1.2639 | 0 | 2.5783 | 0
| 38 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 39 | 0.093873 | 0.11061 | 0.016736 | 0 | 0.093873 | 0
| 40 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 41 | 0.0099703 | 0.0054531 | -0.0045172 | 0 | 0.0099703 | 0
| 42 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 43 | 0.0058635 | 0.010851 | 0.0049871 | 0 | 0.0058635 | 0
| 44 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 45 | 0.049348 | 0.1084 | 0.059048 | 0 | 0.049348 | 0
| 46 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 47 | 1.9495 | 0.84014 | -1.1093 | 0 | 1.9495 | 0
| 48 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
| 49 | 1.6138 | 0.64159 | -0.97217 | 0 | 1.6138 | 0
| 50 | 0.049456 | 0.10839 | 0.058929 | 0 | 0.049456 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 123.9044 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.016734 | 0.0056893 | 0.089625 | 0.0032455 | 0.0086057 | 0.0581 | 0.12317 | 0.20365 | 0.22655 | 0.33743 | 0.48747 | 0.48747 | 0.48747 | 0.48747 | 0.48747 | 0.48747 | 0.48747 | 0.48747
3 |  |  | 2.9425 | 2.9912 | 3.2843 | 5.0979 | 7.098 | 7.4647 | 5.2954 | 3.8134 | 2.8958 | 2.3177 | 1.636 | 1.636 | 1.636 | 1.636 | 1.636 | 1.636 | 1.636 | 1.636
4 |  |  | 0.019268 | 0.032778 | 0.054311 | 0.0097454 | 0.020338 | 0.013189 | 0.0081818 | 0.0025841 | 0.0074495 | 0.0042907 | 0.0090247 | 0.0090247 | 0.0090247 | 0.0090247 | 0.0090247 | 0.0090247 | 0.0090247 | 0.0090247
5 |  |  | 0.0647 | 0.022844 | 0.15433 | 0.018823 | 0.031518 | 0.044399 | 0.03196 | 0.019767 | 0.012372 | 0.010119 | 0.0051477 | 0.0051477 | 0.0051477 | 0.0051477 | 0.0051477 | 0.0051477 | 0.0051477 | 0.0051477
6 |  |  | 0.11515 | 0.019737 | 0.06906 | 0.0061368 | 0.025065 | 0.0077675 | 0.0066937 | 0.0040693 | 0.0029049 | 0.0020482 | 0.0010812 | 0.0010812 | 0.0010812 | 0.0010812 | 0.0010812 | 0.0010812 | 0.0010812 | 0.0010812
7 |  |  | 0.046424 | 0.041014 | 0.020774 | 0.0050883 | 0.026713 | 0.049598 | 0.032813 | 0.019619 | 0.014407 | 0.0098259 | 0.0053342 | 0.0053342 | 0.0053342 | 0.0053342 | 0.0053342 | 0.0053342 | 0.0053342 | 0.0053342
8 |  |  | 0.18926 | 0.040911 | 0.048947 | 0.0026417 | 0.012851 | 0.0028399 | 0.0045149 | 0.0083724 | 0.0051881 | 0.00061731 | 0.011221 | 0.011221 | 0.011221 | 0.011221 | 0.011221 | 0.011221 | 0.011221 | 0.011221
9 |  |  | 2.0675 | 0.47119 | 0.55354 | 0.60142 | 0.941 | 1.0256 | 0.74301 | 0.56273 | 0.44611 | 0.3708 | 0.27465 | 0.27465 | 0.27465 | 0.27465 | 0.27465 | 0.27465 | 0.27465 | 0.27465
10 |  |  | 0.099933 | 0.029332 | 0.044855 | 0.0073311 | 0.0016216 | 0.012691 | 0.01526 | 0.011442 | 0.028253 | 0.031543 | 0.053078 | 0.053078 | 0.053078 | 0.053078 | 0.053078 | 0.053078 | 0.053078 | 0.053078
11 |  |  | 56.1476 | 21.046 | 10.5343 | 8.3389 | 8.2713 | 7.0967 | 6.2075 | 5.7088 | 5.2709 | 4.9132 | 4.3591 | 4.3591 | 4.3591 | 4.3591 | 4.3591 | 4.3591 | 4.3591 | 4.3591
12 |  |  | 0.013663 | 0.036627 | 0.016587 | 0.010192 | 0.0096555 | 0.010827 | 0.0075353 | 0.0033094 | 0.01074 | 0.019211 | 0.042969 | 0.042969 | 0.042969 | 0.042969 | 0.042969 | 0.042969 | 0.042969 | 0.042969
13 |  |  | 45.6948 | 11.0407 | 7.9025 | 5.4737 | 3.5423 | 2.9177 | 2.9554 | 2.7282 | 2.5784 | 2.4589 | 2.2753 | 2.2753 | 2.2753 | 2.2753 | 2.2753 | 2.2753 | 2.2753 | 2.2753
14 |  |  | 0.038701 | 0.032364 | 0.035908 | 0.0081996 | 0.00094171 | 0.0073923 | 0.0099448 | 0.014287 | 0.0045981 | 0.01743 | 0.021424 | 0.021424 | 0.021424 | 0.021424 | 0.021424 | 0.021424 | 0.021424 | 0.021424
15 |  |  | 0.70986 | 0.47303 | 0.37155 | 0.33344 | 0.49963 | 0.53446 | 0.41155 | 0.30295 | 0.24065 | 0.20031 | 0.15448 | 0.15448 | 0.15448 | 0.15448 | 0.15448 | 0.15448 | 0.15448 | 0.15448
16 |  |  | 0.018287 | 0.0091218 | 0.025577 | 0.006101 | 0.015337 | 0.0065173 | 0.0042911 | 0.0056139 | 0.0057741 | 0.0011761 | 0.0067307 | 0.0067307 | 0.0067307 | 0.0067307 | 0.0067307 | 0.0067307 | 0.0067307 | 0.0067307
17 |  |  | 0.010907 | 0.0086444 | 0.016114 | 0.0062226 | 0.02669 | 0.040981 | 0.03052 | 0.017783 | 0.013759 | 0.0094804 | 0.0079644 | 0.0079644 | 0.0079644 | 0.0079644 | 0.0079644 | 0.0079644 | 0.0079644 | 0.0079644
18 |  |  | 0.069418 | 0.0082787 | 0.026956 | 0.0041666 | 0.019846 | 0.0034858 | 0.0052519 | 0.0043867 | 0.0014374 | 0.00080177 | 0.0032857 | 0.0032857 | 0.0032857 | 0.0032857 | 0.0032857 | 0.0032857 | 0.0032857 | 0.0032857
19 |  |  | 0.0055733 | 0.012693 | 0.0055218 | 0.0041283 | 0.02482 | 0.050105 | 0.028752 | 0.021262 | 0.014836 | 0.010677 | 0.0071915 | 0.0071915 | 0.0071915 | 0.0071915 | 0.0071915 | 0.0071915 | 0.0071915 | 0.0071915
20 |  |  | 0.018441 | 0.011776 | 0.022809 | 0.0050305 | 0.013121 | 0.0074317 | 0.0063873 | 0.0055926 | 0.0042396 | 0.00085694 | 0.0070421 | 0.0070421 | 0.0070421 | 0.0070421 | 0.0070421 | 0.0070421 | 0.0070421 | 0.0070421
21 |  |  | 0.027539 | 0.27721 | 0.2324 | 0.23055 | 0.37127 | 0.42461 | 0.30723 | 0.24141 | 0.19353 | 0.16193 | 0.12166 | 0.12166 | 0.12166 | 0.12166 | 0.12166 | 0.12166 | 0.12166 | 0.12166
22 |  |  | 0.041585 | 0.032859 | 0.021101 | 0.0071305 | 0.0027272 | 0.0088705 | 0.0090947 | 0.0032669 | 0.010612 | 0.011826 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968
23 |  |  | 6.5562 | 3.4959 | 2.9667 | 2.2238 | 2.1432 | 1.8719 | 1.5276 | 1.4204 | 1.3076 | 1.2082 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536
24 |  |  | 0.0078956 | 0.031784 | 0.010833 | 0.010709 | 0.0046133 | 0.0097479 | 0.0083117 | 0.0059959 | 0.009761 | 0.014432 | 0.026172 | 0.026172 | 0.026172 | 0.026172 | 0.026172 | 0.026172 | 0.026172 | 0.026172
25 |  |  | 5.5201 | 3.0355 | 1.9719 | 1.2222 | 0.9832 | 0.83161 | 1.0041 | 0.92171 | 0.86674 | 0.81864 | 0.74369 | 0.74369 | 0.74369 | 0.74369 | 0.74369 | 0.74369 | 0.74369 | 0.74369
26 |  |  | 0.024335 | 0.026543 | 0.012852 | 0.0078033 | 0.0040417 | 0.0078653 | 0.00901 | 0.0071088 | 0.004476 | 0.0071113 | 0.008698 | 0.008698 | 0.008698 | 0.008698 | 0.008698 | 0.008698 | 0.008698 | 0.008698
27 |  |  | 0.19615 | 0.14918 | 0.21833 | 0.15284 | 0.21063 | 0.23376 | 0.20632 | 0.15869 | 0.13222 | 0.11292 | 0.090321 | 0.090321 | 0.090321 | 0.090321 | 0.090321 | 0.090321 | 0.090321 | 0.090321
28 |  |  | 0.024676 | 0.0020604 | 0.010075 | 0.0040954 | 0.015528 | 0.0045454 | 0.0040901 | 0.0055306 | 0.0058693 | 0.0011388 | 0.0052749 | 0.0052749 | 0.0052749 | 0.0052749 | 0.0052749 | 0.0052749 | 0.0052749 | 0.0052749
29 |  |  | 0.0040788 | 0.010088 | 0.023134 | 0.0065366 | 0.025396 | 0.03279 | 0.027461 | 0.01582 | 0.011409 | 0.0082531 | 0.0059385 | 0.0059385 | 0.0059385 | 0.0059385 | 0.0059385 | 0.0059385 | 0.0059385 | 0.0059385
30 |  |  | 0.044163 | 0.0047847 | 0.02268 | 0.0040932 | 0.018457 | 0.0039923 | 0.0057534 | 0.0021808 | 0.00074625 | 0.00028568 | 0.0026781 | 0.0026781 | 0.0026781 | 0.0026781 | 0.0026781 | 0.0026781 | 0.0026781 | 0.0026781
31 |  |  | 0.0052247 | 0.0074381 | 0.0057287 | 0.0058487 | 0.024819 | 0.04936 | 0.027712 | 0.020617 | 0.013919 | 0.0098142 | 0.0070035 | 0.0070035 | 0.0070035 | 0.0070035 | 0.0070035 | 0.0070035 | 0.0070035 | 0.0070035
32 |  |  | 0.033701 | 0.014235 | 0.0071096 | 0.0050984 | 0.0083149 | 0.0059756 | 0.0057701 | 0.0062634 | 0.0063278 | 0.00038619 | 0.008077 | 0.008077 | 0.008077 | 0.008077 | 0.008077 | 0.008077 | 0.008077 | 0.008077
33 |  |  | 0.044712 | 0.14987 | 0.16364 | 0.13074 | 0.21885 | 0.24801 | 0.17654 | 0.14044 | 0.11245 | 0.094879 | 0.070097 | 0.070097 | 0.070097 | 0.070097 | 0.070097 | 0.070097 | 0.070097 | 0.070097
34 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
35 |  |  | 3.4105 | 1.6959 | 1.1328 | 0.99759 | 0.83578 | 0.70613 | 0.54722 | 0.5149 | 0.47648 | 0.44098 | 0.38895 | 0.38895 | 0.38895 | 0.38895 | 0.38895 | 0.38895 | 0.38895 | 0.38895
36 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
37 |  |  | 2.5783 | 1.3145 | 0.92036 | 0.57518 | 0.42703 | 0.32525 | 0.41831 | 0.36559 | 0.33391 | 0.30806 | 0.27228 | 0.27228 | 0.27228 | 0.27228 | 0.27228 | 0.27228 | 0.27228 | 0.27228
38 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
39 |  |  | 0.093873 | 0.11061 | 0.12385 | 0.087026 | 0.13156 | 0.14794 | 0.14139 | 0.10604 | 0.08652 | 0.073003 | 0.058372 | 0.058372 | 0.058372 | 0.058372 | 0.058372 | 0.058372 | 0.058372 | 0.058372
40 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
41 |  |  | 0.0099703 | 0.0054531 | 0.017643 | 0.005916 | 0.022045 | 0.026033 | 0.026001 | 0.014356 | 0.011651 | 0.008334 | 0.0063742 | 0.0063742 | 0.0063742 | 0.0063742 | 0.0063742 | 0.0063742 | 0.0063742 | 0.0063742
42 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
43 |  |  | 0.0058635 | 0.010851 | 0.010943 | 0.0060325 | 0.026418 | 0.050864 | 0.027315 | 0.020634 | 0.014324 | 0.0098979 | 0.0064947 | 0.0064947 | 0.0064947 | 0.0064947 | 0.0064947 | 0.0064947 | 0.0064947 | 0.0064947
44 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
45 |  |  | 0.049348 | 0.1084 | 0.10131 | 0.088403 | 0.1639 | 0.17906 | 0.12757 | 0.10312 | 0.083643 | 0.070487 | 0.05267 | 0.05267 | 0.05267 | 0.05267 | 0.05267 | 0.05267 | 0.05267 | 0.05267
46 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
47 |  |  | 1.9495 | 0.84014 | 0.59741 | 0.51691 | 0.41051 | 0.33982 | 0.28264 | 0.27732 | 0.26482 | 0.25051 | 0.22847 | 0.22847 | 0.22847 | 0.22847 | 0.22847 | 0.22847 | 0.22847 | 0.22847
48 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
49 |  |  | 1.6138 | 0.64159 | 0.44211 | 0.32705 | 0.16811 | 0.11257 | 0.17976 | 0.15708 | 0.14829 | 0.14097 | 0.13514 | 0.13514 | 0.13514 | 0.13514 | 0.13514 | 0.13514 | 0.13514 | 0.13514
50 |  |  | 0.049456 | 0.10839 | 0.1013 | 0.088459 | 0.16391 | 0.17902 | 0.12755 | 0.10311 | 0.083633 | 0.07048 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666 | 0.052666
| Ithd |  | 73.1594 | 24.5284 | 14.1535 | 11.5879 | 11.817 | 11.0237 | 8.9628 | 7.6562 | 6.7944 | 6.2014 | 5.4053 | 5.4053 | 5.4053 | 5.4053 | 5.4053 | 5.4053 | 5.4053 | 5.4053

## E01 (hidden)
E01 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A | 0 | PU Load |  |  | 0.985 | PF
18 Pulse | 54 |  | 1 | 0 |  |  |  |  | 0 | Harmonic multiplier
|  | 0.1 | 0.5 | 0.4 | 0 | 0.1
| 1 | 0 | 1 |  |  | 100 | 0 | Ifund
| 2 | 1.2515 | 1.1887 | -0.062836 | 0 | 1.2515 | 0
| 3 | 2.3272 | 2.2103 | -0.11684 | 0 | 2.3272 | 0
| 4 | 0.17996 | 0.17092 | -0.0090352 | 0 | 0.17996 | 0
| 5 | 4.0848 | 3.8797 | -0.20509 | 0 | 4.0848 | 0
| 6 | 0.02454 | 0.023308 | -0.0012321 | 0 | 0.02454 | 0
| 7 | 1.999 | 1.8986 | -0.10036 | 0 | 1.999 | 0
| 8 | 0.077709 | 0.073807 | -0.0039016 | 0 | 0.077709 | 0
| 9 | 0.077709 | 0.073807 | -0.0039016 | 0 | 0.077709 | 0
| 10 | 0.02454 | 0.023308 | -0.0012321 | 0 | 0.02454 | 0
| 11 | 2.0442 | 1.9415 | -0.10263 | 0 | 2.0442 | 0
| 12 | 0.053169 | 0.0505 | -0.0026695 | 0 | 0.053169 | 0
| 13 | 1.0221 | 0.97076 | -0.051316 | 0 | 1.0221 | 0
| 14 | 0.053169 | 0.0505 | -0.0026695 | 0 | 0.053169 | 0
| 15 | 0.15542 | 0.14761 | -0.0078032 | 0 | 0.15542 | 0
| 16 | 0.02454 | 0.023308 | -0.0012321 | 0 | 0.02454 | 0
| 17 | 1.7174 | 1.6311 | -0.086225 | 0 | 1.7174 | 0
| 18 | 0.10225 | 0.097115 | -0.0051337 | 0 | 0.10225 | 0
| 19 | 1.9781 | 1.8788 | -0.099316 | 0 | 1.9781 | 0
| 20 | 0.053169 | 0.0505 | -0.0026695 | 0 | 0.053169 | 0
| 21 | 0.10225 | 0.097115 | -0.0051337 | 0 | 0.10225 | 0
| 22 | 0.077709 | 0.073807 | -0.0039016 | 0 | 0.077709 | 0
| 23 | 0.4137 | 0.39293 | -0.020771 | 0 | 0.4137 | 0
| 24 | 0.077709 | 0.073807 | -0.0039016 | 0 | 0.077709 | 0
| 25 | 0.45541 | 0.43255 | -0.022865 | 0 | 0.45541 | 0
| 26 | 0.053169 | 0.0505 | -0.0026695 | 0 | 0.053169 | 0
| 27 | 0.077709 | 0.073807 | -0.0039016 | 0 | 0.077709 | 0
| 28 | 0.02454 | 0.023308 | -0.0012321 | 0 | 0.02454 | 0
| 29 | 0.60838 | 0.57783 | -0.030545 | 0 | 0.60838 | 0
| 30 | 0.053169 | 0.0505 | -0.0026695 | 0 | 0.053169 | 0
| 31 | 0.50061 | 0.47547 | -0.025134 | 0 | 0.50061 | 0
| 32 | 0.0027879 | 0.0013237 | -0.0014642 | 0 | 0.0027879 | 0
| 33 | 0.011017 | 0.0060232 | -0.0049939 | 0 | 0.011017 | 0
| 34 | 0.0034475 | 0.00076609 | -0.0026814 | 0 | 0.0034475 | 0
| 35 | 0.17556 | 0.099478 | -0.076086 | 0 | 0.17556 | 0
| 36 | 0.0029493 | 0.0011945 | -0.0017548 | 0 | 0.0029493 | 0
| 37 | 0.14169 | 0.083607 | -0.058079 | 0 | 0.14169 | 0
| 38 | 0.0023675 | 0.00071401 | -0.0016535 | 0 | 0.0023675 | 0
| 39 | 0.0085599 | 0.0044384 | -0.0041215 | 0 | 0.0085599 | 0
| 40 | 0.0017729 | 0.00058689 | -0.0011861 | 0 | 0.0017729 | 0
| 41 | 0.12175 | 0.064725 | -0.057023 | 0 | 0.12175 | 0
| 42 | 0.0019389 | 0.00098297 | -0.00095589 | 0 | 0.0019389 | 0
| 43 | 0.099372 | 0.056137 | -0.043236 | 0 | 0.099372 | 0
| 44 | 0.0015372 | 0.00057017 | -0.00096705 | 0 | 0.0015372 | 0
| 45 | 0.0074262 | 0.0038783 | -0.0035479 | 0 | 0.0074262 | 0
| 46 | 0.00055168 | 0.00078322 | 0.00023154 | 0 | 0.00055168 | 0
| 47 | 0.081578 | 0.051879 | -0.0297 | 0 | 0.081578 | 0
| 48 | 0.0020715 | 0.0013487 | -0.00072276 | 0 | 0.0020715 | 0
| 49 | 0.070106 | 0.043519 | -0.026587 | 0 | 0.070106 | 0
| 50 | 0.00092245 | 0.00062294 | -0.00029951 | 0 | 0.00092245 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 100.2046 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01 | Data from simulations of 18P using auto-xfmr, 2002
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 1.2515 | 1.1887 | 1.1073 | 0.97909 | 0.8743 | 0.81591 | 0.78072 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313 | 0.76313
3 |  |  | 2.3272 | 2.2103 | 2.059 | 1.8206 | 1.6257 | 1.5172 | 1.4517 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419 | 1.419
4 |  |  | 0.17996 | 0.17092 | 0.15922 | 0.14078 | 0.12572 | 0.11732 | 0.11226 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973 | 0.10973
5 |  |  | 4.0848 | 3.8797 | 3.614 | 3.1956 | 2.8536 | 2.663 | 2.5482 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
6 |  |  | 0.02454 | 0.023308 | 0.021711 | 0.019198 | 0.017143 | 0.015998 | 0.015308 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963
7 |  |  | 1.999 | 1.8986 | 1.7686 | 1.5638 | 1.3965 | 1.3032 | 1.247 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189 | 1.2189
8 |  |  | 0.077709 | 0.073807 | 0.068753 | 0.060793 | 0.054287 | 0.050661 | 0.048476 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384
9 |  |  | 0.077709 | 0.073807 | 0.068753 | 0.060793 | 0.054287 | 0.050661 | 0.048476 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384
10 |  |  | 0.02454 | 0.023308 | 0.021711 | 0.019198 | 0.017143 | 0.015998 | 0.015308 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963
11 |  |  | 2.0442 | 1.9415 | 1.8086 | 1.5992 | 1.428 | 1.3326 | 1.2752 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 1.2465
12 |  |  | 0.053169 | 0.0505 | 0.047041 | 0.041595 | 0.037144 | 0.034663 | 0.033168 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421
13 |  |  | 1.0221 | 0.97076 | 0.90428 | 0.79959 | 0.71402 | 0.66632 | 0.63759 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323 | 0.62323
14 |  |  | 0.053169 | 0.0505 | 0.047041 | 0.041595 | 0.037144 | 0.034663 | 0.033168 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421
15 |  |  | 0.15542 | 0.14761 | 0.13751 | 0.12159 | 0.10857 | 0.10132 | 0.096953 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768 | 0.094768
16 |  |  | 0.02454 | 0.023308 | 0.021711 | 0.019198 | 0.017143 | 0.015998 | 0.015308 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963
17 |  |  | 1.7174 | 1.6311 | 1.5194 | 1.3435 | 1.1997 | 1.1196 | 1.0713 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472
18 |  |  | 0.10225 | 0.097115 | 0.090464 | 0.079991 | 0.07143 | 0.066659 | 0.063785 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348
19 |  |  | 1.9781 | 1.8788 | 1.7501 | 1.5475 | 1.3819 | 1.2896 | 1.234 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062 | 1.2062
20 |  |  | 0.053169 | 0.0505 | 0.047041 | 0.041595 | 0.037144 | 0.034663 | 0.033168 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421
21 |  |  | 0.10225 | 0.097115 | 0.090464 | 0.079991 | 0.07143 | 0.066659 | 0.063785 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348 | 0.062348
22 |  |  | 0.077709 | 0.073807 | 0.068753 | 0.060793 | 0.054287 | 0.050661 | 0.048476 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384
23 |  |  | 0.4137 | 0.39293 | 0.36602 | 0.32364 | 0.28901 | 0.2697 | 0.25807 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226 | 0.25226
24 |  |  | 0.077709 | 0.073807 | 0.068753 | 0.060793 | 0.054287 | 0.050661 | 0.048476 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384
25 |  |  | 0.45541 | 0.43255 | 0.40293 | 0.35628 | 0.31815 | 0.2969 | 0.2841 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777 | 0.2777
26 |  |  | 0.053169 | 0.0505 | 0.047041 | 0.041595 | 0.037144 | 0.034663 | 0.033168 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421
27 |  |  | 0.077709 | 0.073807 | 0.068753 | 0.060793 | 0.054287 | 0.050661 | 0.048476 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384 | 0.047384
28 |  |  | 0.02454 | 0.023308 | 0.021711 | 0.019198 | 0.017143 | 0.015998 | 0.015308 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963 | 0.014963
29 |  |  | 0.60838 | 0.57783 | 0.53826 | 0.47594 | 0.42501 | 0.39662 | 0.37952 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097 | 0.37097
30 |  |  | 0.053169 | 0.0505 | 0.047041 | 0.041595 | 0.037144 | 0.034663 | 0.033168 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421 | 0.032421
31 |  |  | 0.50061 | 0.47547 | 0.44291 | 0.39163 | 0.34972 | 0.32636 | 0.31229 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525 | 0.30525
32 |  |  | 0.0027879 | 0.0013237 | 0.0011495 | 0.0014343 | 0.0015485 | 0.0016057 | 0.0016401 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573
33 |  |  | 0.011017 | 0.0060232 | 0.0026793 | 0.0037314 | 0.0033518 | 0.0030693 | 0.0028991 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814 | 0.002814
34 |  |  | 0.0034475 | 0.00076609 | 0.0015637 | 0.0016172 | 0.0015212 | 0.0014635 | 0.0014287 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113
35 |  |  | 0.17556 | 0.099478 | 0.070211 | 0.069212 | 0.068836 | 0.068575 | 0.068419 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834 | 0.06834
36 |  |  | 0.0029493 | 0.0011945 | 0.00054435 | 0.00097566 | 0.0011679 | 0.0012649 | 0.0013233 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525 | 0.0013525
37 |  |  | 0.14169 | 0.083607 | 0.057462 | 0.054969 | 0.055176 | 0.055338 | 0.055435 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484 | 0.055484
38 |  |  | 0.0023675 | 0.00071401 | 0.0039184 | 0.001274 | 0.00079266 | 0.00061996 | 0.00051592 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391 | 0.00046391
39 |  |  | 0.0085599 | 0.0044384 | 0.0034292 | 0.0040998 | 0.0034562 | 0.0030361 | 0.0027831 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566 | 0.0026566
40 |  |  | 0.0017729 | 0.00058689 | 0.0034023 | 0.00090498 | 0.0010854 | 0.0013063 | 0.0014394 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059 | 0.0015059
41 |  |  | 0.12175 | 0.064725 | 0.059073 | 0.047507 | 0.045628 | 0.044959 | 0.044557 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355 | 0.044355
42 |  |  | 0.0019389 | 0.00098297 | 0.0011071 | 0.00097349 | 0.00065306 | 0.00046494 | 0.00035162 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495 | 0.00029495
43 |  |  | 0.099372 | 0.056137 | 0.046219 | 0.040627 | 0.03904 | 0.038288 | 0.037834 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607 | 0.037607
44 |  |  | 0.0015372 | 0.00057017 | 0.0040375 | 0.0010281 | 0.00099035 | 0.0011022 | 0.0011695 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032 | 0.0012032
45 |  |  | 0.0074262 | 0.0038783 | 0.0026961 | 0.0019358 | 0.0022088 | 0.0024028 | 0.0025196 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578 | 0.002578
46 |  |  | 0.00055168 | 0.00078322 | 0.0032791 | 0.00022078 | 0.00019161 | 0.00030769 | 0.00037762 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258 | 0.00041258
47 |  |  | 0.081578 | 0.051879 | 0.048587 | 0.033064 | 0.032415 | 0.032659 | 0.032807 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288 | 0.03288
48 |  |  | 0.0020715 | 0.0013487 | 0.00026277 | 0.00077532 | 0.00087371 | 0.00090907 | 0.00093038 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103 | 0.00094103
49 |  |  | 0.070106 | 0.043519 | 0.038812 | 0.029641 | 0.02829 | 0.027841 | 0.027571 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436 | 0.027436
50 |  |  | 0.00092245 | 0.00062294 | 0.002824 | 0.00046968 | 0.0007107 | 0.00096055 | 0.0011111 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863 | 0.0011863
| Ithd |  | 6.4 | 6.0746 | 5.6579 | 5.0029 | 4.4677 | 4.1695 | 3.9898 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9

## F01 (hidden)
F01 | Drive row | 38490.0179 | Isc/Iload | 0 | 0.1 | %Z | 0 | A fund | 0 | A rated fund |  |  | 0.995 | PF
ULH (AFE) | 66 |  | 1 | 0 |  |  | 0 | rated HP
|  | 0.1 | 0.5 | 0.4 | 0 | 0.1 | 0
| 1 | 0 | 1 |  |  | 100 | 0 | Ifund |  |  |  | Corrected 7/5/2022 rh
| 2 | 0.72 | 0.72 | 0 | 0 | 0.72 | 0 | [5 empty] | I1 modified
| 3 | 0.62 | 0.62 | 0 | 0 | 0.62 | 0 | [5 empty] | J1 and K1 added
| 4 | 0.5 | 0.5 | 0 | 0 | 0.5 | 0 | [5 empty] | H5:H53 modified using J$1 instead of H$4
| 5 | 2.54 | 2.54 | 0 | 0 | 2.54 | 0
| 6 | 0.2 | 0.2 | 0 | 0 | 0.2 | 0
| 7 | 0.47 | 0.47 | 0 | 0 | 0.47 | 0
| 8 | 0.15 | 0.15 | 0 | 0 | 0.15 | 0
| 9 | 0.45 | 0.45 | 0 | 0 | 0.45 | 0
| 10 | 0.18 | 0.18 | 0 | 0 | 0.18 | 0
| 11 | 0.28 | 0.28 | 0 | 0 | 0.28 | 0
| 12 | 0.26 | 0.26 | 0 | 0 | 0.26 | 0
| 13 | 0.44 | 0.44 | 0 | 0 | 0.44 | 0
| 14 | 0.34 | 0.34 | 0 | 0 | 0.34 | 0
| 15 | 0.28 | 0.28 | 0 | 0 | 0.28 | 0
| 16 | 0.26 | 0.26 | 0 | 0 | 0.26 | 0
| 17 | 0.29 | 0.29 | 0 | 0 | 0.29 | 0
| 18 | 0.17 | 0.17 | 0 | 0 | 0.17 | 0
| 19 | 0.31 | 0.31 | 0 | 0 | 0.31 | 0
| 20 | 0.28 | 0.28 | 0 | 0 | 0.28 | 0
| 21 | 0.33 | 0.33 | 0 | 0 | 0.33 | 0
| 22 | 0.23 | 0.23 | 0 | 0 | 0.23 | 0
| 23 | 0.89 | 0.89 | 0 | 0 | 0.89 | 0
| 24 | 0.35 | 0.35 | 0 | 0 | 0.35 | 0
| 25 | 0.41 | 0.41 | 0 | 0 | 0.41 | 0
| 26 | 0.42 | 0.42 | 0 | 0 | 0.42 | 0
| 27 | 0.69 | 0.69 | 0 | 0 | 0.69 | 0
| 28 | 0.53 | 0.53 | 0 | 0 | 0.53 | 0
| 29 | 0.81 | 0.81 | 0 | 0 | 0.81 | 0
| 30 | 0.33 | 0.33 | 0 | 0 | 0.33 | 0
| 31 | 0.68 | 0.68 | 0 | 0 | 0.68 | 0
| 32 | 0.29 | 0.29 | 0 | 0 | 0.29 | 0
| 33 | 0.26 | 0.26 | 0 | 0 | 0.26 | 0
| 34 | 0.24 | 0.24 | 0 | 0 | 0.24 | 0
| 35 | 0.41 | 0.41 | 0 | 0 | 0.41 | 0
| 36 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0
| 37 | 0.28 | 0.28 | 0 | 0 | 0.28 | 0
| 38 | 0.08 | 0.08 | 0 | 0 | 0.08 | 0
| 39 | 0.15 | 0.15 | 0 | 0 | 0.15 | 0
| 40 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0
| 41 | 0.27 | 0.27 | 0 | 0 | 0.27 | 0
| 42 | 0.06 | 0.06 | 0 | 0 | 0.06 | 0
| 43 | 0.14 | 0.14 | 0 | 0 | 0.14 | 0
| 44 | 0.07 | 0.07 | 0 | 0 | 0.07 | 0
| 45 | 0.06 | 0.06 | 0 | 0 | 0.06 | 0
| 46 | 0.09 | 0.09 | 0 | 0 | 0.09 | 0
| 47 | 0.23 | 0.23 | 0 | 0 | 0.23 | 0
| 48 | 0.07 | 0.07 | 0 | 0 | 0.07 | 0
| 49 | 0.15 | 0.15 | 0 | 0 | 0.15 | 0
| 50 | 0.07 | 0.07 | 0 | 0 | 0.07 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 100.0656 | 0 | Itotal
[6 empty] | % | A
Reference Tables:
|  | Rsc | 1000 | 200 | 100 | 50 | 33.3333 | 25 | 20 | 16.6667 | 14.2857 | 12.5 | 10 | 8.3333 | 7.1429 | 5.5556 | 4.7619 | 1 | 0.1 | 0.01 | measured | reduced | original
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | values | due to | values
harm no |  | %Z | 0.1 | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 21 | 100 | 1000 | 10000 | in lab | 5th Vthd
|  | column no | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2 |  |  | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 0.345
3 |  |  | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 |  | 0.3675
4 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.225
5 |  |  | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.74 | 2.54 | 0.7425
6 |  |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2025
7 |  |  | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 |  | 1.365
8 |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  | 0.225
9 |  |  | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 |  | 0.315
10 |  |  | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 |  | 0.4275
11 |  |  | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 |  | 0.915
12 |  |  | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 |  | 0.54
13 |  |  | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 |  | 0.6525
14 |  |  | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 |  | 0.63
15 |  |  | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 |  | 0.6525
16 |  |  | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 |  | 0.6
17 |  |  | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 |  | 0.9675
18 |  |  | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 |  | 0.54
19 |  |  | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 |  | 0.57
20 |  |  | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 |  | 0.6825
21 |  |  | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 |  | 0.6
22 |  |  | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 |  | 0.6
23 |  |  | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 |  | 0.9975
24 |  |  | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  | 0.6
25 |  |  | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 |  | 0.7125
26 |  |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 |  | 0.255
27 |  |  | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 |  | 0.255
28 |  |  | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 |  | 0.285
29 |  |  | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 |  | 0.225
30 |  |  | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 |  | 0.225
31 |  |  | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 |  | 0.1425
32 |  |  | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 |  | 0.1725
33 |  |  | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 |  | 0.03
34 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 |  | 0.03
35 |  |  | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 |  | 0.03
36 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.03
37 |  |  | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 |  | 0.03
38 |  |  | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  | 0.03
39 |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  | 0.03
40 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.03
41 |  |  | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 |  | 0.03
42 |  |  | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 |  | 0.03
43 |  |  | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 |  | 0.06
44 |  |  | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 |  | 0.03
45 |  |  | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 |  | 0.03
46 |  |  | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 |  | 0.03
47 |  |  | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 |  | 0.03
48 |  |  | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 |  | 0.03
49 |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  | 0.03
50 |  |  | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 |  | 0.03
| Iharm | Arms | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.6221 | 3.765 |  | 3.2883

## G01 (hidden)
G01 | Drive row | Data from | Copy of | If delta/wye | % Load | Transformer | Currents |  | Other Values for Drives row 78
Custom | 78 | Sum column | column | (Y/N) | Multiplier | Pri cur | Transferred to
System |  | AG | C |  |  | multiplier | Sum column
|  |  | values | Y | 0 | 0 | AF |  |  | Pin rated [kW] | Pin actual [kW] | PF disp | Qin [kVAR] | Din [kVAD] | Sin [kVA] | Ireal rated [A] | Ireal actual [A] | Ireact [A] | Iharm [A] | Ifund [A] | Itotal [A] | Ithd [%]
| 1 real | 0 |  | 1 | 0 | 0 | 0 |  | Data from | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 react | 0 |  | 1 | 0 | 0 | 0 |  | Power column B
| 1 fund | 0 |  | 1 | 0 | 0 | 0 | Ifund | Copy of above | [6 empty] | 389.4948 | 389.4948 | 13.9825 | 26.8733 | 389.7457 | 390.671 | 6.8951
| 2 | 0 |  | 1 | 0 | 0 | 0 |  | values
| 3 | 0 |  | 1 | 0 | 0 | 0 | [8 empty] | currents at primary of second transformer
| 4 | 0 |  | 1 | 0 | 0 | 0 |  | Values | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | -1 | 0 | 0 | 0 |  | transferred to Drives row 78
| 6 | 0 |  | 1 | 0 | 0 | 0 |  | includes drive and lin load data
| 7 | 0 |  | -1 | 0 | 0 | 0
| 8 | 0 |  | 1 | 0 | 0 | 0 |  |  | Transformer primary voltage |  | 1
| 9 | 0 |  | 1 | 0 | 0 | 0 |  |  | Transformer secondary voltage
| 10 | 0 |  | 1 | 0 | 0 | 0
| 11 | 0 |  | 1 | 0 | 0 | 0 |  |  | Transformer primary current mult |  | 0
| 12 | 0 |  | 1 | 0 | 0 | 0
| 13 | 0 |  | 1 | 0 | 0 | 0
| 14 | 0 |  | 1 | 0 | 0 | 0 |  |  | Be sure to change the % Loaded on the Input tab by adding the
| 15 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | kVA for linear loads on Custom System
| 16 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | +kVA for linear loads on system without custom system
| 17 | 0 |  | -1 | 0 | 0 | 0 |  |  |  | = total kVA for linear loads on system with custom system
| 18 | 0 |  | 1 | 0 | 0 | 0
| 19 | 0 |  | -1 | 0 | 0 | 0
| 20 | 0 |  | 1 | 0 | 0 | 0
| 21 | 0 |  | 1 | 0 | 0 | 0
| 22 | 0 |  | 1 | 0 | 0 | 0
| 23 | 0 |  | 1 | 0 | 0 | 0
| 24 | 0 |  | 1 | 0 | 0 | 0
| 25 | 0 |  | 1 | 0 | 0 | 0
| 26 | 0 |  | 1 | 0 | 0 | 0
| 27 | 0 |  | 1 | 0 | 0 | 0
| 28 | 0 |  | 1 | 0 | 0 | 0
| 29 | 0 |  | 1 | 0 | 0 | 0
| 30 | 0 |  | 1 | 0 | 0 | 0
| 31 | 0 |  | 1 | 0 | 0 | 0
| 32 | 0 |  | 1 | 0 | 0 | 0
| 33 | 0 |  | 1 | 0 | 0 | 0
| 34 | 0 |  | 1 | 0 | 0 | 0
| 35 | 0 |  | 1 | 0 | 0 | 0
| 36 | 0 |  | 1 | 0 | 0 | 0
| 37 | 0 |  | 1 | 0 | 0 | 0
| 38 | 0 |  | 1 | 0 | 0 | 0
| 39 | 0 |  | 1 | 0 | 0 | 0
| 40 | 0 |  | 1 | 0 | 0 | 0
| 41 | 0 |  | 1 | 0 | 0 | 0
| 42 | 0 |  | 1 | 0 | 0 | 0
| 43 | 0 |  | 1 | 0 | 0 | 0
| 44 | 0 |  | 1 | 0 | 0 | 0
| 45 | 0 |  | 1 | 0 | 0 | 0
| 46 | 0 |  | 1 | 0 | 0 | 0
| 47 | 0 |  | 1 | 0 | 0 | 0
| 48 | 0 |  | 1 | 0 | 0 | 0
| 49 | 0 |  | 1 | 0 | 0 | 0
| 50 | 0 |  | 1 | 0 | 0 | 0
[5 empty] | thd | 0 | 0 | Iharm
[5 empty] | total | 0 | 0 | Itotal
[6 empty] | % | A